## Intro
Current calculation tool can serve a basis for elaboration of energy audit report in buildings.
Tables with input data and calculations have to be attached as an annex to the energy audit report.
Indications for use:
Tables can be multiplied or modified depending on various situations, rows and columns can be deleted, added or combined.
Cells which require input data or text
Cells with automatic calculations or text
Cells which are advised to remain unchanged, but not mandatory.
The energy auditor is free to add graphs, or improve the tool in any way he considers relevant
Energy consumption can be expressed in various units of measure, further all calculations to be done in kWh.
Calculations related to water savings are not considered by the current tool, it can be developed further by the auditor in case if it will be required.
The values and contents (formulas, links etc.) of the spreadsheet provided as a input data for energy audit report is in full responsability of the energy auditor.

## Sheet1
Республика, вилоят, жой | Ойлик ўртача ҳарорат | [11 empty] | Ўртача йиллик ҳарорат | Энг кичик мутлақ ҳарорат | Энг катта мутлақ ҳарорат | Энг иссиқ ойдаги энг катта ўртача ҳарорат | Энг совуқ ойдаги энг кичик ўртача ҳарорат
| I | II | III | IV | V | VI | VII | VIII | IX | X | XI | XII
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
Тошкент вилояти
Тошкент | 1,9 | 3,9 | 9,4 | 15,5 | 20,5 | 25,8 | 27,8 | 26,2 | 20,6 | 13,8 | 8,5 | 3,5 | 14,8 | -0.015285 | 44.6/1997 | 35,6 | -1,5
Янгийўл | 0,4 | 2,9 | 9,0 | 15,6 | 21,1 | 26,3 | 27,8 | 25,7 | 20,2 | 13,5 | 7,3 | 1,7 | 14,3 | -0.01658 | 45.5/1998 | 36,2 | -3,1
Туябўғуз | 1,1 | 3,5 | 9,3 | 16,0 | 21,2 | 26,3 | 27,8 | 26,1 | 21,1 | 14,5 | 8,3 | 2,6 | 14,8 | -0.013763 | 42.7/1983 | 35,2 | -2,1
Кўкорол | -0,1 | 2,5 | 8,6 | 15,3 | 20,3 | 24,7 | 25,7 | 23,6 | 18,4 | 12,4 | 6,6 | 1,2 | 13,3 | -0.016353 | 46.1/1944 | 34,3 | -3,8
Далварзин | 1,5 | 4,1 | 9,9 | 16,5 | 21,8 | 26,7 | 27,7 | 25,4 | 20,2 | 14,1 | 8,3 | 2,9 | 14,9 | -0.018135 | 43.5/2005 | 35,2 | -2,2
Бекобод | 1,6 | 3,8 | 9,8 | 16,4 | 21,6 | 26,4 | 27,6 | 25,5 | 20,4 | 14,2 | 8,6 | 3,0 | 14,9 | -0.015648 | 43.8/1944 | 34,8 | -0,9
Олмалиқ | 1,5 | 3,7 | 9,3 | 15,8 | 21,1 | 26,6 | 28,2 | 26,4 | 21,1 | 14,6 | 8,6 | 3,2 | 15,0 | -0.010359 | 43.5/1993 | 34,8 | -2,2
Ангрен | 0,9 | 2,3 | 7,4 | 13,6 | 18,5 | 23,7 | 25,8 | 24,5 | 19,5 | 12,8 | 7,7 | 2,9 | 13,3 | -0.013953 | 42.6/1944 | 32,1 | -2,7
Бошқизилсой | -0,4 | 0,9 | 5,4 | 11,4 | 15,9 | 21,1 | 23,6 | 22,6 | 17,5 | 10,9 | 6,1 | 1,6 | 11,4 | -0.015084 | 40.0/1984 | 30,0 | -3,4
Сўқоқ | 0,1 | 1,0 | 5,1 | 11,2 | 15,7 | 21,0 | 23,2 | 22,4 | 17,6 | 11,4 | 6,6 | 2,3 | 11,5 | -0.012867 | 37.2/1983 | 28,6 | -3,3
Дукент | -2,9 | -2,4 | 1,5 | 7,5 | 11,9 | 17,0 | 19,6 | 19,2 | 14,7 | 8,3 | 3,6 | -0,6 | 8,1 | -0.012443 | 35.2/1983,2008 | 25,4 | -5,9
Чимён | -2,9 | -2,1 | 2,0 | 8,4 | 13,1 | 18,3 | 20,8 | 20,4 | 15,5 | 9,0 | 4,0 | -0,6 | 8,8 | -0.01185 | 35.2/2008 | 26,1 | -6,0
Пскем | -2,9 | -1,7 | 3,2 | 10,1 | 14,3 | 18,8 | 21,8 | 21,7 | 16,8 | 9,9 | 4,5 | -0,7 | 9,7 | -0.013845 | 41.7/1983 | 29,8 | -6,5
Ойгаинг | -9,8 | -8,8 | -4,3 | 1,5 | 7,7 | 12,2 | 14,9 | 15,3 | 10,6 | 3,4 | -2,9 | -7,7 | 2,7 | -0.016049 | 36.0/1976 | 23,2 | -14,1

## Building_data
Description | Unit | Value
Total net heated floor area | [m²] | 2515.415
Total net heated volume | [m³] | 7546.245
Total net cooled floor area (if any) | [m²] | 0
Duration of the heating season (as per NCM M.01.02:2016, Annex A) | [days] | 163
Average inside temperature during heating season in non-operation hours (standardized) | [°C] | 14
Average inside temperature during heating season in operation hours (standardized) | [°C] | 22
Medium outside temperature during heating season (as per NCM M.01.02:2016, Annex A) | [°C] | 3.9
Coldest 5 days outside temperature (design temperature, as per СНиП 2.01.01-82) | [°C] | -14
Operation hours during heating season | [h/y] | 1630
Non-operation hours during heating season | [h/y] | 14
Operation hours per day | [h/d] | 10
Average inside enthalpy during cooling period for +24°C and relative humidity of 50% | [kJ/kg] | 48.4
Average outside enthalpy during cooling period | [kJ/kg] | 59.5
Outside enthalpy during the hottest summer day | [kJ/kg] | 69.13
Average number of people inside the building | [No of people] | 418

## Envelope
Block | Orientation | Side of the building | Element | Walls | [5 empty] | Windows | [8 empty] | Doors
|  |  |  | Dimension |  |  | Area |  |  | Dimension |  | Type |  |  | Area |  |  | Perimeter of window sills [m] | Dimension |  | Type |  |  | Area |  |  | Perimeter of door sills [m]
|  |  |  | Lenght [m] | Height of the wall in contact with environment [m] | Height of the wall in contact with the ground [m] | Brut area of the wall in contact with environment [m2] | Area of the wall in contact with the ground [m2] | Net area of the wall in contact with environment [m2] | Lenght [m] | Height [m] | Win 1 [units] | Win 2 [units] | Win 3 [units] | Win 1 [m2] | Win 2 [m2] | Win 3 [m2] |  | Lenght [m] | Height [m] | D 1 [units] | D 2 [units] | D 3 [units] | D 1 [m2] | D 2 [m2] | D 3 [m2] |  | 256.62
3-DMTT | N | P1 | W1 | 50.7 | 6.6 |  | 334.62 | 0 | 277.82 | 1.2 | 1.8 |  |  | 21 | 0 | 0 | 45.36 | 126 | 2.2 | 2.6 | 2 |  |  | 11.44 | 0 | 0 | 19.2 | 45.36 | S | 79.02
|  |  | Socle 1. (unheated space) | 50.7 | 0.55 |  | 27.885 | 0 | 22.485 | 1 | 1.8 |  |  | 1 | 0 | 0 | 1.8 | 5.6 | 0.9 | 2 | 2 |  |  | 3.6 | 0 | 0 | 11.6 | 1.8 | N | 86.4
[7 empty] | 0 | 0 | -2.56 | 0.8 | 0.8 |  |  | 4 | 0 | 0 | 2.56 | 12.8 | [5 empty] | 0 | 0 | 0 | 0 | 2.56 | E | 10.8
| W | P2 | W1 | 13.2 | 6.6 |  | 87.12 | 0 | 75.24 | 1.2 | 1.8 |  |  | 3 | 0 | 0 | 6.48 | 18 | 0.9 | 2 | 3 |  |  | 5.4 | 0 | 0 | 17.4 | 6.48 | W | 14.76
|  |  | Socle 1. (unheated space) | 13.2 | 0.55 |  | 7.26 | 0 | 0.06 | 1 | 1.8 |  |  | 4 | 0 | 0 | 7.2 | 22.4 | [5 empty] | 0 | 0 | 0 | 0 | 7.2 | SW | 0
| S | P3 | W1 | 24.5 | 6.6 |  | 161.7 | 0 | 135.78 | 1.2 | 1.8 |  |  | 12 | 0 | 0 | 25.92 | 72 | [5 empty] | 0 | 0 | 0 | 0 | 25.92 | SE | 0
|  |  | Socle 1. (unheated space) | 24.5 | 0.55 |  | 13.475 | 0 | 12.195 | 0.8 | 0.8 |  |  | 2 | 0 | 0 | 1.28 | 6.4 | [5 empty] | 0 | 0 | 0 | 0 | 1.28 | NE | 0
| W | P4 | W1 | 13.25 | 3.3 |  | 43.725 | 0 | 40.125 | 1 | 1.8 |  |  | 1 | 0 | 0 | 1.8 | 5.6 | 0.9 | 2 | 1 |  |  | 1.8 | 0 | 0 | 5.8 | 1.8 | NW | 0
|  |  | Socle 1. (unheated space) | 13.25 | 0.55 |  | 7.2875 | 0 | 7.2875 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| N | P5 | W1 | 24.5 | 6.6 |  | 161.7 | 0 | 135.78 | 1.2 | 1.8 |  |  | 12 | 0 | 0 | 25.92 | 72 | [5 empty] | 0 | 0 | 0 | 0 | 25.92
|  |  | Socle 1. (unheated space) | 24.5 | 0.55 |  | 13.475 | 0 | 12.195 | 0.8 | 0.8 |  |  | 2 | 0 | 0 | 1.28 | 6.4 | [5 empty] | 0 | 0 | 0 | 0 | 1.28
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| W | P6 | W1 | 13.2 | 6.6 |  | 87.12 | 0 | 75.24 | 1.2 | 1.8 |  |  | 3 | 0 | 0 | 6.48 | 18 | 0.9 | 2 | 3 |  |  | 5.4 | 0 | 0 | 17.4 | 6.48
|  |  | Socle 1. (unheated space) | 13.2 | 0.55 |  | 7.26 | 0 | -1.74 | 1 | 1.8 |  |  | 5 | 0 | 0 | 9 | 28 | [5 empty] | 0 | 0 | 0 | 0 | 9
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| S | P7 | W1 | 50.7 | 6.6 |  | 334.62 | 0 | 275.66 | 1.2 | 1.8 |  |  | 22 | 0 | 0 | 47.52 | 132 | 2.2 | 2.6 | 2 |  |  | 11.44 | 0 | 0 | 19.2 | 47.52
|  |  | Socle 1. (unheated space) | 50.7 | 0.55 |  | 27.885 | 0 | 21.725 | 0.8 | 0.8 |  |  | 4 | 0 | 0 | 2.56 | 12.8 | 0.9 | 2 | 2 |  |  | 3.6 | 0 | 0 | 11.6 | 2.56
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| E | P8 | W1 | 13.2 | 6.6 |  | 87.12 | 0 | 79.2 | 1.2 | 1.8 |  |  | 2 | 0 | 0 | 4.32 | 12 | 0.9 | 2 | 2 |  |  | 3.6 | 0 | 0 | 11.6 | 4.32
|  |  | Socle 1. (unheated space) | 13.2 | 0.55 |  | 7.26 | 0 | 0.06 | 1 | 1.8 |  |  | 4 | 0 | 0 | 7.2 | 22.4 | [5 empty] | 0 | 0 | 0 | 0 | 7.2
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| N | P9 | W1 | 21.3 | 6.6 |  | 140.58 | 0 | 125.82 | 1.2 | 1.8 |  |  | 6 | 0 | 0 | 12.96 | 36 | 0.9 | 2 | 1 |  |  | 1.8 | 0 | 0 | 5.8 | 12.96
|  |  | Socle 1. (unheated space) | 21.3 | 0.55 |  | 11.715 | 0 | 9.915 | 1 | 1.8 |  |  | 1 | 0 | 0 | 1.8 | 5.6 | [5 empty] | 0 | 0 | 0 | 0 | 1.8
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| E | P10 | W1 | 13.25 | 3.3 |  | 43.725 | 0 | 39.375 | [5 empty] | 0 | 0 | 0 | 0 | 1.5 | 2.9 | 1 |  |  | 4.35 | 0 | 0 | 8.8 | 0
|  |  | Socle 1. (unheated space) | 13.25 | 0.55 |  | 7.2875 | 0 | 7.2875 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| S | P11 | W1 | 21.3 | 6.6 |  | 140.58 | 0 | 133.56 | 1.9 | 1.8 |  |  | 1 | 0 | 0 | 3.42 | 7.4 | 0.9 | 2 | 2 |  |  | 3.6 | 0 | 0 | 11.6 | 3.42
|  |  | Socle 1. (unheated space) | 21.3 | 0.55 |  | 11.715 | 0 | 9.555 | 1.2 | 1.8 |  |  | 1 | 0 | 0 | 2.16 | 6 | [5 empty] | 0 | 0 | 0 | 0 | 2.16
[7 empty] | 0 | 0 | -19.8 | 1 | 1.8 |  |  | 11 | 0 | 0 | 19.8 | 61.6 | [5 empty] | 0 | 0 | 0 | 0 | 19.8
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| E | P12 | W1 | 13.2 | 6.6 |  | 87.12 | 0 | 75.24 | 1.2 | 1.8 |  |  | 3 | 0 | 0 | 6.48 | 18 | 0.9 | 2 | 3 |  |  | 5.4 | 0 | 0 | 17.4 | 6.48
|  |  | Socle 1. (unheated space) | 13.2 | 0.55 |  | 7.26 | 0 | 0.06 | 1 | 1.8 |  |  | 4 | 0 | 0 | 7.2 | 22.4 | [5 empty] | 0 | 0 | 0 | 0 | 7.2
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| S | P13 | W1 | 4.3 | 3.3 |  | 14.19 | 0 | 12.03 | 1.2 | 1.8 |  |  | 1 | 0 | 0 | 2.16 | 6 | [5 empty] | 0 | 0 | 0 | 0 | 2.16
|  |  | Socle 1. (unheated space) | 4.3 | 0.55 |  | 2.365 | 0 | 0.565 | 1 | 1.8 |  |  | 1 | 0 | 0 | 1.8 | 5.6 | [5 empty] | 0 | 0 | 0 | 0 | 1.8
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| N | P14 | W1 | 4.3 | 3.3 |  | 14.19 | 0 | 12.03 | 1.2 | 1.8 |  |  | 1 | 0 | 0 | 2.16 | 6 | [5 empty] | 0 | 0 | 0 | 0 | 2.16
|  |  | Socle 1. (unheated space) | 4.3 | 0.55 |  | 2.365 | 0 | 2.365 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
|  | Total | W1 | [5 empty] | 1492.9 | Total area by type [m2] |  |  |  |  | 0 | 0 | 256.62 | [6 empty] | 61.43 | 0 | 0
|  |  | W2 (unheated) | [5 empty] | 0
|  |  | Socle 1. (heated space) | [5 empty] | 0 | Total area [m2] |  |  |  |  | 256.62 | [8 empty] | 61.43
|  |  | Socle 1. (unheated space) | [5 empty] | 104.015
[10 empty] | Total sills perimeter [m] | [7 empty] | 747 | [8 empty] | 157.4
|  |  | Socle 2 | 0 |  |  |  |  | 0
[12 empty] | 0 | 0 | 132
|  | Space name | Brut area of one floor [m²] | Number of floors | Total brut heated area [m²] | Net height of one floor | Perimeter of the building [m] | Thickness of exterior walls [m] | Total area of the walls in section [m²] | Net heated area [m²] | Net heated volume [m³] | [17 empty] | Element | Description of windows and doors before renovation | Type | Uvalue [W/m²K] | Area [m²]
[29 empty] | Window | PVC framed, 3 camera, double glazed [3-12-3mm] | Win1 | 2.56 | 0
|  | A blok | 669.24 | 2 | 1338.48 | 3 | 127.8 | 0.4 | 102.24 | 1236.24 | 3708.72 | [18 empty] | Wooden double framed [3-50-3mm] | Win2 | 2.78 | 0
|  | B blok | 669.24 | 2 | 1338.48 | 3 | 127.8 | 0.4 | 102.24 | 1236.24 | 3708.72 | [18 empty] | Aluminum frame 4-40-4 | Win3 | 2.94 | 256.62
|  | C blok | 56.975 | 1 | 56.975 | 3 | 35.1 | 0.4 | 14.04 | 42.935 | 128.805
[5 empty] | 0 |  |  |  | 0 | 0 | 0 | [17 empty] | Door | Aluminum frame 4-40-4, double glazed [3-12-3mm] | D1 | 3.5 | 61.43
[5 empty] | 0 |  |  |  | 0 | 0 | 0 | [18 empty] | Wooden – 50mm | D2 | 4 | 0
[5 empty] | 0 |  |  |  | 0 | 0 | 0 | [18 empty] | Metal | D3 | 5.88 | 0
[5 empty] | 0 |  |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  |  | 0 | 0 | 0
|  | Total |  |  | 2733.935 |  |  |  |  | 2515.415 | 7546.245
[29 empty] | Element | Description of windows and doors after renovation | Type | Uvalue [W/m²K]
[29 empty] | Window | PVC framed, 5 camera, double glazed [4mm (Low-e < 0.1) - 20 Ar - 4mm] . | Win4 | 1.5
[29 empty] | Door | PVC framed, 5 camera, sandwich panel 28 mm, double glazed [4mm (Low-e < 0.1) - 20 Ar - 4mm] . | D4 | 1.8
Types of walls
[30 empty] | Description of existing walls | Type | Area [m²]
[30 empty] | Internal plaster 10mm, Prefabricated concrete panels filled with ceramzit 350 mm, external plaster 10mm. | W1 | 1492.9
[30 empty] | Internal plaster 10mm, Prefabricated concrete panels filled with ceramzit 350 mm | W2 (unheated) | 0 | heat losses do not calc
[30 empty] | Socle area in contact with environment. Prefabricated concrete panels filled with ceramzit 350 mm, Concrete/sand mix 20mm, Decorative stone 30mm. | Socle 1. (heated space) | 0
[30 empty] | Socle area in contact with environment. Concrete 600mm, Concrete/sand mix 20mm, Decorative stone 30mm. | Socle 1. (unheated space) | 104.015
[30 empty] | Socle area in contact with the ground. Concrete 600mm | Socle 2 | 0
Types of floors
[30 empty] | Description of existing floors | Type | Area [m²]
[30 empty] | Floor in contact with unheated space. Concrete panel 220mm, cheramzit 50mm, cocnrete sand mix 50mm, Marble 30mm | F1 | 1279.175
[30 empty] | Floor in contact with environment. Concrete panel 220mm, cheramzit 50mm, cocnrete sand mix 50mm, Marble 30mm | F2
Types of roof
[30 empty] | Description of existing roof | Type | Area [m²]
[30 empty] | Roof in contact with unheated space (technical floor). Internal plaster 10mm, Concrete Panel 220mm, Expanded clay 50mm, Concrete 50mm | R1 | 1279.175
[30 empty] | Roof in contact with environment. Internal plaster 10mm, Concrete Panel 220mm, Cheramzit 50mm, Concrete 50mm, Bitumen 6mm | R2
Perimeter pavement area
Perimeter pavement area
P1
P5
P9
P2
P6
P4
P12
P8
P10
P3
P11
P13
P7
P14
Note on N19: Saidmurodjon Khamdamov: ikki qanotli
Note on P19: Saidmurodjon Khamdamov: ikki qanotli
Note on N24: Saidmurodjon Khamdamov: ikki qanotli
Note on P24: Saidmurodjon Khamdamov: ikki qanotli
Note on N27: Saidmurodjon Khamdamov: ikki qanotli
Note on P27: Saidmurodjon Khamdamov: ikki qanotli
Note on N32: Saidmurodjon Khamdamov: ikki qanotli
Note on P32: Saidmurodjon Khamdamov: ikki qanotli
Note on N35: Saidmurodjon Khamdamov: ikki qanotli
Note on P35: Saidmurodjon Khamdamov: ikki qanotli
Note on N44: Saidmurodjon Khamdamov: ikki qanotli
Note on P44: Saidmurodjon Khamdamov: ikki qanotli
Note on N52: Saidmurodjon Khamdamov: ikki qanotli
Note on P52: Saidmurodjon Khamdamov: ikki qanotli
Note on N56: Saidmurodjon Khamdamov: ikki qanotli
Note on P56: Saidmurodjon Khamdamov: ikki qanotli
Note on N59: Saidmurodjon Khamdamov: ikki qanotli
Note on P59: Saidmurodjon Khamdamov: ikki qanotli

## Consumption
GAS |  | Anul 2023 |  |  | Anul 2024 |  |  | Anul 2025 |  |  | Average for the past 3 years (Baseline)
№ | Davr | Consum | Expenses | Tarif [so'm/m3] | Consum | Expenses | Tarif [so'm/m3] | Consum | Expenses | Tarif [so'm/m3] | Consum | Expenses | Tarif [so'm/m3] |  |  | According to latest tariff |  |  | 700000 | so'm/gcal
|  | [m3] | [so'm] |  | [m3] | [so'm] |  | [m3] | [so'm] |  | [kWh] | [so'm] |  |  |  |  | Thermal |  | 601.8917 | so'm/kWh
1 | January | 7274 | 18185000 | 2500 | 5691 | 14227500 | 2500 | 6976 | 17440000 | 2500 | 63146.5 | 69461150 | 1100 |  |  |  | Electrical |  | 1100 | so'm/kWh |  | 8887
2 | February | 5399 | 13497500 | 2500 | 5304 | 13260000 | 2500 | 5774 | 14435000 | 2500 | 52177.1667 | 57394883.3333 | 1100 |  |  |  | GAS |  | 2500 | so'm/m3
3 | March | 1710 | 4275000 | 2500 | 3218 | 8045000 | 2500 | 2989 | 7472500 | 2500 | 25070.5 | 27577550 | 1100
4 | April | 645 | 1612500 | 2500 | 514 | 1285000 | 2500 | 79 | 197500 | 2500 | 3920.3333 | 4312366.6667 | 1100
5 | May | 564 | 1410000 | 2500 | 557 | 1392500 | 2500 | 66 | 165000 | 2500 | 3758.8333 | 4134716.6667 | 1100
6 | June | 609 | 1522500 | 2500 | 519 | 1297500 | 2500 | 54 | 135000 | 2500 | 3743 | 4117300 | 1100
7 | July | 614 | 1535000 | 2500 | 526 | 1315000 | 2500 | 47 | 117500 | 2500 | 3758.8333 | 4134716.6667 | 1100
8 | August | 571 | 1427500 | 2500 | 106 | 265000 | 2500 | 1054 | 2635000 | 2500 | 5481.5 | 6029650 | 1100
9 | September | 205 | 512500 | 2500 | 95 | 237500 | 2500 | 62 | 155000 | 2500 | 1146.3333 | 1260966.6667 | 1100
10 | October | 1138 | 2845000 | 2500 | 1062 | 2655000 | 2500 | 65 | 162500 | 2500 | 7172.5 | 7889750 | 1100
11 | November | 3196 | 7990000 | 2500 | 1609 | 4022500 | 2500 | 2933 | 7332500 | 2500 | 24503.6667 | 26954033.3333 | 1100
12 | December | 4965 | 12412500 | 2500 | 5476 | 13690000 | 2500 | 4239 | 10597500 | 2500 | 46486.6667 | 51135333.3333 | 1100
TOTAL |  | 26890 | 67225000 |  | 24677 | 61692500 |  | 24338 | 60845000 |  | 240365.8333 | 264402416.6667
Electrical Energy |  | Anul 2023 |  |  | Anul 2024 |  |  | Anul 2025 |  |  | Average for the past 3 years (Baseline)
№ | Davr | Consum | Expenses | Tarif [so'm/kWh] | Consum | Expenses | Tarif [so'm/kWh] | Consum | Expenses | Tarif [so'm/kWh] | Consum | Expenses | Tarif [so'm/kWh]
|  | [kWh] | [so'm] |  | [kWh] | [so'm] |  | [kWh] | [so'm] |  | [kWh] | [so'm]
1 | January | 4211 | 3789900 | 900 | 7119 | 6407100 | 900 | 6699 | 6029100 | 900 | 6009.6667 | 6610633.3333 | 1100
2 | February | 4389 | 3950100 | 900 | 6447 | 5802300 | 900 | 5964 | 5367600 | 900 | 5600 | 6160000 | 1100
3 | March | 3633 | 3269700 | 900 | 5439 | 4895100 | 900 | 4893 | 4403700 | 900 | 4655 | 5120500 | 1100
4 | April | 6111 | 5499900 | 900 | 4641 | 4176900 | 900 | 4473 | 4025700 | 900 | 5075 | 5582500 | 1100
5 | May | 4095 | 3685500 | 900 | 4630 | 4167000 | 900 | 4059 | 3653100 | 900 | 4261.3333 | 4687466.6667 | 1100
6 | June | 2604 | 2343600 | 900 | 3620 | 3258000 | 900 | 4000 | 3600000 | 900 | 3408 | 3748800 | 1100
7 | July | 2900 | 2610000 | 900 | 3499 | 3149100 | 900 | 4138 | 3724200 | 900 | 3512.3333 | 3863566.6667 | 1100
8 | August | 2770 | 2493000 | 900 | 4157 | 3741300 | 900 | 3964 | 3567600 | 900 | 3630.3333 | 3993366.6667 | 1100
9 | September | 3780 | 3402000 | 900 | 4296 | 3866400 | 900 | 3663 | 3296700 | 900 | 3913 | 4304300 | 1100
10 | October | 3507 | 3156300 | 900 | 5124 | 4611600 | 900 | 4486 | 4037400 | 900 | 4372.3333 | 4809566.6667 | 1100
11 | November | 5607 | 5046300 | 900 | 5565 | 5008500 | 900 | 5751 | 5175900 | 900 | 5641 | 6205100 | 1100
12 | December | 5586 | 5027400 | 900 | 6111 | 5499900 | 900 | 6204 | 5583600 | 900 | 5967 | 6563700 | 1100
TOTAL |  | 49193 | 44273700 |  | 60648 | 54583200 |  | 58294 | 52464600 |  | 56045 | 61649500
Energie Termică |  | Anul 2023 |  |  | Anul 2024 |  |  | Anul 2025 |  |  | Average for the past 3 years (Baseline)
№ | Davr | Consum | Expenses | Tarif [so'm/m3] | Consum | Expenses | Tarif [so'm/m3] | Consum | Expenses | Tarif [so'm/m3] | Consum | Expenses | Tarif [so'm/m3]
|  | [m3] | [so'm] |  | [m3] | [so'm] |  | [m3] | [so'm] |  | [kWh] | [so'm]
1 | January |  |  | 1122 |  |  | 1122 |  |  | 1122 | 0 | 0 | 601.8917 | [8 empty] | 8887
2 | February |  |  | 1122 |  |  | 1122 |  |  | 1122 | 0 | 0 | 601.8917
3 | March |  |  | 1122 |  |  | 1122 |  |  | 1122 | 0 | 0 | 601.8917
4 | April |  |  | 1122 |  |  | 1122 |  |  | 1122 | 0 | 0 | 601.8917
5 | May |  |  | 1122 |  |  | 1122 |  |  | 1122 | 0 | 0 | 601.8917 | #DIV/0! | 0 |  | #DIV/0! | 0 |  | #DIV/0! | 0
6 | June |  |  | 1122 |  |  | 1122 |  |  | 1122 | 0 | 0 | 601.8917 | [6 empty] | #DIV/0!
7 | July |  |  | 1122 |  |  | 1122 |  |  | 1122 | 0 | 0 | 601.8917 | [6 empty] | #DIV/0!
8 | August |  |  | 1122 |  |  | 1122 |  |  | 1122 | 0 | 0 | 601.8917 | [6 empty] | #DIV/0!
9 | September |  |  | 1122 |  |  | 1122 |  |  | 1122 | 0 | 0 | 601.8917 | [6 empty] | #DIV/0!
10 | October |  |  | 1122 |  |  | 1122 |  |  | 1122 | 0 | 0 | 601.8917
11 | November |  |  | 1122 |  |  | 1122 |  |  | 1772 | 0 | 0 | 601.8917
12 | December |  |  | 1122 |  |  | 1122 |  |  | 1772 | 0 | 0 | 601.8917
TOTAL |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
For DHW preparation the average (baseline energy consumption) should be also calculated in kWh
For other types of fuels like biomass, natural gas, coal etc. the same principle to be applied.

## Weather (hidden)
Normative Weather | [12 empty] | I propose to delete this page in general, because:
1. We have normative values in one single standard, for different climatic zones and different heating durations (3 zones x 2 types of heating duration = 6 tables)
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 2. We never use actual weather in calculations, only the normative because we don't have an open acces to weather data, it costs a lot of money and unfortunately even the Ministry cannot afford to by it yet to update the 40yo database from standards
Ambient temp | -1.7 | -0.7 | 4.5 | 11 | 17 | 19.7 | 21.1 | 21 | 15.3 | 10.6 | 5.4 | -0.8 | 3. These tables shouldn't be here because this data is fixed by the standard and is not an input data.
North | 9 | 14 | 25 | 33 | 46 | 53 | 53 | 37 | 27 | 19 | 12 | 9
East | 17 | 32 | 63 | 87 | 111 | 105 | 117 | 100 | 76 | 53 | 28 | 16
South | 47 | 72 | 112 | 109 | 104 | 90 | 100 | 111 | 119 | 115 | 75 | 49
West | 19 | 32 | 66 | 87 | 106 | 103 | 108 | 97 | 79 | 59 | 30 | 19
Global | 27 | 49 | 100 | 140 | 180 | 177 | 187 | 164 | 122 | 81 | 41 | 26
Dew point | -3.6 | -3.4 | -0.3 | 4.7 | 10.4 | 13.3 | 15.5 | 14.9 | 10.7 | 6.9 | 2.5 | -2.7
Sky temp | -11.7 | -12.4 | -8.4 | -2.4 | 4.5 | 7.4 | 9.6 | 9.7 | 4.6 | -0.2 | -4.9 | -11.4
Ground temp | -1.7 | -0.7 | 4.5 | 11 | 17 | 19.7 | 21.1 | 21 | 15.3 | 10.6 | 5.4 | -0.8
Actual weather data of |  |  | year
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Ambient temp | -1.7 | -0.7 | 4.5 | 11 | 17 | 19.7 | 21.1 | 21 | 15.3 | 10.6 | 5.4 | -0.8
North | 9 | 14 | 25 | 33 | 46 | 53 | 53 | 37 | 27 | 19 | 12 | 9
East | 17 | 32 | 63 | 87 | 111 | 105 | 117 | 100 | 76 | 53 | 28 | 16
South | 47 | 72 | 112 | 109 | 104 | 90 | 100 | 111 | 119 | 115 | 75 | 49
West | 19 | 32 | 66 | 87 | 106 | 103 | 108 | 97 | 79 | 59 | 30 | 19
Global | 27 | 49 | 100 | 140 | 180 | 177 | 187 | 164 | 122 | 81 | 41 | 26
Dew point | -3.6 | -3.4 | -0.3 | 4.7 | 10.4 | 13.3 | 15.5 | 14.9 | 10.7 | 6.9 | 2.5 | -2.7
Sky temp | -11.7 | -12.4 | -8.4 | -2.4 | 4.5 | 7.4 | 9.6 | 9.7 | 4.6 | -0.2 | -4.9 | -11.4
Ground temp | -1.7 | -0.7 | 4.5 | 11 | 17 | 19.7 | 21.1 | 21 | 15.3 | 10.6 | 5.4 | -0.8
Actual weather data of |  |  | year
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Ambient temp | -1.7 | -0.7 | 4.5 | 11 | 17 | 19.7 | 21.1 | 21 | 15.3 | 10.6 | 5.4 | -0.8
North | 9 | 14 | 25 | 33 | 46 | 53 | 53 | 37 | 27 | 19 | 12 | 9
East | 17 | 32 | 63 | 87 | 111 | 105 | 117 | 100 | 76 | 53 | 28 | 16
South | 47 | 72 | 112 | 109 | 104 | 90 | 100 | 111 | 119 | 115 | 75 | 49
West | 19 | 32 | 66 | 87 | 106 | 103 | 108 | 97 | 79 | 59 | 30 | 19
Global | 27 | 49 | 100 | 140 | 180 | 177 | 187 | 164 | 122 | 81 | 41 | 26
Dew point | -3.6 | -3.4 | -0.3 | 4.7 | 10.4 | 13.3 | 15.5 | 14.9 | 10.7 | 6.9 | 2.5 | -2.7
Sky temp | -11.7 | -12.4 | -8.4 | -2.4 | 4.5 | 7.4 | 9.6 | 9.7 | 4.6 | -0.2 | -4.9 | -11.4
Ground temp | -1.7 | -0.7 | 4.5 | 11 | 17 | 19.7 | 21.1 | 21 | 15.3 | 10.6 | 5.4 | -0.8
Actual weather data of |  |  | year
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Ambient temp | -1.7 | -0.7 | 4.5 | 11 | 17 | 19.7 | 21.1 | 21 | 15.3 | 10.6 | 5.4 | -0.8
North | 9 | 14 | 25 | 33 | 46 | 53 | 53 | 37 | 27 | 19 | 12 | 9
East | 17 | 32 | 63 | 87 | 111 | 105 | 117 | 100 | 76 | 53 | 28 | 16
South | 47 | 72 | 112 | 109 | 104 | 90 | 100 | 111 | 119 | 115 | 75 | 49
West | 19 | 32 | 66 | 87 | 106 | 103 | 108 | 97 | 79 | 59 | 30 | 19
Global | 27 | 49 | 100 | 140 | 180 | 177 | 187 | 164 | 122 | 81 | 41 | 26
Dew point | -3.6 | -3.4 | -0.3 | 4.7 | 10.4 | 13.3 | 15.5 | 14.9 | 10.7 | 6.9 | 2.5 | -2.7
Sky temp | -11.7 | -12.4 | -8.4 | -2.4 | 4.5 | 7.4 | 9.6 | 9.7 | 4.6 | -0.2 | -4.9 | -11.4
Ground temp | -1.7 | -0.7 | 4.5 | 11 | 17 | 19.7 | 21.1 | 21 | 15.3 | 10.6 | 5.4 | -0.8

## U-values
| Calculation of Uvalue for external wall before renovation (W1) | [5 empty] | Calculation of Uvalue for external wall after renovation (W1)
| Layers |  | Thickness | Thermal conductivity |  | Thermal resistance | Layers |  | Thickness | Thermal conductivity |  | Thermal resistance |  | Rezistența termică a suprafeței din Interior / Exterior [m²K/W] - SM SR EN ISO 6946
[14 empty] | Rezistența termică a suprafeței în m2K/W |  | Rint | Rext
|  |  | [m] | [W/mK] |  | [m²K/W] |  |  | [m] | [W/mK] |  | [m²K/W]
| 1 | Internal plaster | 0.002 | 0.7 |  | 0.0028571 | 1 | Internal plaster | 0.002 | 0.7 |  | 0.0028571 |  | Tashqi muhit bilan aloqada bo'lgan vertikal element (masalan, devor) |  | 0.115 | 0.04 | Material de construcție | λ,W/(m∙K) | Column1
| 2 | Concrete/sand mix | 0.01 | 0.76 |  | 0.013158 | 2 | Concrete/sand mix | 0.01 | 0.76 |  | 0.013158 |  | Isitilgan makon bilan aloqada bo'lgan devor |  | 0.115 | 0.115 | Internal plaster | 0.7
| 3 | Bricks | 0.38 | 0.7 |  | 0.54286 | 3 | Bricks | 0.38 | 0.7 |  | 0.54286 |  | Yer bilan aloqada bo'lgan devor (vertikal) |  | 2.1 | 0 | External plaster | 0.76
| 4 | Concrete/sand mix | 0.01 | 0.76 |  | 0.013158 | 4 | Concrete/sand mix | 0.01 | 0.76 |  | 0.013158 |  | Tom tashqi muhit bilan aloqada |  | 0.115 | 0.04 | Concrete | 1.92
| 5 | [5 empty] | 5 | [6 empty] | Isitilmagan makon ostidagi shift |  | 0.115 | 0.083 | Concrete mixed with EPS (G-Sort) | 0.07
| 6 | [5 empty] | 6 | Mineral wool MW | 0.1 | 0.038 |  | 2.6316 |  | Ochiq maydon ustidagi pol |  | 0.115 | 0.04 | Concrete with stones | 1.74
[7 empty] | 7 | Ruberoid | 0.005 | 0.17 |  | 0.029412 | [5 empty] | Polistirolbeton | 0.055
[7 empty] | 8 | External plaster | 0.005 | 0.76 |  | 0.0065789
| Total |  | 0.402 |  |  | 0.57203 | Total |  | 0.512 |  |  | 3.2396 |  | Isitilgan maydon ustidagi pol |  | 0.115 | 0.166 | Concrete with expanded clay | 0.52
| Thermal resistance of interior surface |  |  | Rint | [m²K/W] | 0.115 | Thermal resistance of interior surface |  |  | Rint | [m²K/W] | 0.115 |  | Yer bilan aloqada pol |  | 2.1 | 0 | Aerated concrete (YTONG) | 0.41
| Thermal resistance of exterior surface |  |  | Rext | [m²K/W] | 0.04 | Thermal resistance of exterior surface |  |  | Rext | [m²K/W] | 0.04 | [5 empty] | Aggregated slug (from boilers) | 0.76
| Heat transfer coefficient (U value) |  |  |  | [W/m²K] | 1.3755 | Heat transfer coefficient (U value) |  |  |  | [W/m²K] | 0.29459 | [5 empty] | Ruberoid | 0.17
[18 empty] | Bitumen polimeric materials | 0.27
[18 empty] | Wood (pine) | 0.29
[18 empty] | Mosaic | 1.74
[18 empty] | Marble | 2.91
[18 empty] | Granit | 3.49
[18 empty] | Concrete/sand mix | 0.76
[18 empty] | Limestone | 0.73
[18 empty] | Bricks | 0.7
[18 empty] | Hollow bricks | 0.58
[18 empty] | Linoleum | 0.35
[18 empty] | Expanded clay | 0.17
[18 empty] | Tile | 1.1
[18 empty] | Clay layer with straw | 0.65
[15 empty] | roof |  |  | Expanded polysterene EPS | 0.038
[18 empty] | Extruded polysterene XPS | 0.035
| Calculation of Uvalue for external socle before renovation (Socle1)(heated space) | [5 empty] | Calculation of Uvalue for external socle after renovation (Socle1)(heated space) | [7 empty] | floor |  |  | Mineral wool MW | 0.038
| Layers |  | Thickness | Thermal conductivity |  | Thermal resistance | Layers |  | Thickness | Thermal conductivity |  | Thermal resistance | [5 empty] | Magnesium oxide plate | 0.21
[18 empty] | Concrete hollow panels | 1.295 | Bo'shliqli beton panel 220mm
|  |  | [m] | [W/mK] |  | [m²K/W] |  |  | [m] | [W/mK] |  | [m²K/W] | [5 empty] | Decorative stone | 2.1
| 1 | Concrete with stones | 0.6 | 1.74 |  | 0.34483 | 1 | Concrete with stones | 0.6 | 1.74 |  | 0.34483 | [5 empty] | Sintipon prokladka | 0.04
| 2 | Concrete/sand mix | 0.02 | 0.76 |  | 0.026316 | 2 | Concrete/sand mix | 0.02 | 0.76 |  | 0.026316 | [5 empty] | Gidro-bugʻ izolyatsiyasi (Ustki) | 0.4
| 3 | Decorative stone | 0.03 | 2.1 |  | 0.014286 | 3 | Decorative stone | 0.03 | 2.1 |  | 0.014286 | [5 empty] | Tunika shifer | 0.01
| 4 | [5 empty] | 4 | Mineral wool MW | 0.1 | 0.038 |  | 2.6316 | [5 empty] | Pol taxta | 0.29
| 5 | [5 empty] | 5 | Clay layer with straw | 0.004 | 0.65 |  | 0.0061538 | [5 empty] | Gips (Гипс) | 0.35
| 6 | [5 empty] | 6 | External plaster | 0.003 | 0.76 |  | 0.0039474 | [5 empty] | Gipsokarton (Гипсокартон) | 0.19
| Total |  | 0.65 |  |  | 0.38543 | Total |  | 0.757 |  |  | 3.0271 | [5 empty] | Tsement-qum qorishmasi | 0.76
| Thermal resistance of interior surface |  |  | Rint | [m²K/W] | 0.115 | Thermal resistance of interior surface |  |  | Rint | [m²K/W] | 0.115 | [5 empty] | Ohak-qum qorishmasi | 0.7
| Thermal resistance of exterior surface |  |  | Rext | [m²K/W] | 0.04 | Thermal resistance of exterior surface |  |  | Rext | [m²K/W] | 0.04 | [5 empty] | Parket, laminat, linoleum | 0.38
| Heat transfer coefficient (U value) |  |  |  | [W/m²K] | 1.8504 | Heat transfer coefficient (U value) |  |  |  | [W/m²K] | 0.31426 | [5 empty] | Mineral wool MW 150 | 0.22
| Calculation of Uvalue for external socle before renovation (Socle2) | [5 empty] | Calculation of Uvalue for external socle before renovation (Socle2)
| Layers |  | Thickness | Thermal conductivity |  | Thermal resistance | Layers |  | Thickness | Thermal conductivity |  | Thermal resistance
|  |  | [m] | [W/mK] |  | [m²K/W] |  |  | [m] | [W/mK] |  | [m²K/W]
| 1 | Concrete | 0.6 | 1.92 |  | 0.3125 | 1 | Concrete | 0.6 | 1.92 |  | 0.3125
| 2 | Concrete/sand mix | 0.03 | 0.76 |  | 0.039474 | 2 | Concrete/sand mix | 0.03 | 0.76 |  | 0.039474
| 3 | Concrete with stones | 0.02 | 1.74 |  | 0.011494 | 3 | Concrete with stones | 0.02 | 1.74 |  | 0.011494
| 4 | [5 empty] | 4 | Mineral wool MW | 0.1 | 0.038 |  | 2.6316
| 5 | [5 empty] | 5 | Clay layer with straw | 0.004 | 0.65 |  | 0.0061538
| 6 | [5 empty] | 6 | External plaster | 0.003 | 0.76 |  | 0.0039474
| Total |  | 0.65 |  |  | 0.36347 | Total |  | 0.757 |  |  | 3.0051
| Thermal resistance of interior surface |  |  | Rint | [m²K/W] | 2.1 | Thermal resistance of interior surface |  |  | Rint | [m²K/W] | 2.1
| Thermal resistance of exterior surface |  |  | Rext | [m²K/W] | 0 | Thermal resistance of exterior surface |  |  | Rext | [m²K/W] | 0
| Heat transfer coefficient (U value) |  |  |  | [W/m²K] | 0.40593 | Heat transfer coefficient (U value) |  |  |  | [W/m²K] | 0.19588
| Calculation of Uvalue for external roof before renovation (R1) | [5 empty] | Calculation of Uvalue for external roof after renovation (R1)
| Layers |  | Thickness | Thermal conductivity |  | Thermal resistance | Layers |  | Thickness | Thermal conductivity |  | Thermal resistance
|  |  | [m] | [W/mK] |  | [m²K/W] |  |  | [m] | [W/mK] |  | [m²K/W]
| 1 | Internal plaster | 0.01 | 0.7 |  | 0.014286 | 1 | Internal plaster | 0.01 | 0.7 |  | 0.014286
| 2 | Concrete hollow panels | 0.22 | 1.295 |  | 0.16988 | 2 | Concrete hollow panels | 0.22 | 1.295 |  | 0.16988
| 3 | Concrete/sand mix | 0.05 | 0.76 |  | 0.065789 | 3 | Concrete/sand mix | 0.05 | 0.76 |  | 0.065789
| 4 | Bitumen polimeric materials | 0.01 | 0.27 |  | 0.037037 | 4 | Bitumen polimeric materials | 0.01 | 0.27 |  | 0.037037
| 5 | [5 empty] | 5 | Polistirolbeton | 0.15 | 0.055 |  | 2.7273
| 6 | [5 empty] | 6
| Total |  | 0.29 |  |  | 0.287 | Total |  | 0.44 |  |  | 3.0143
| Thermal resistance of interior surface |  |  | Rint | [m²K/W] | 0.115 | Thermal resistance of interior surface |  |  | Rint | [m²K/W] | 0.115
| Thermal resistance of exterior surface |  |  | Rext | [m²K/W] | 0.083 | Thermal resistance of exterior surface |  |  | Rext | [m²K/W] | 0.083
| Heat transfer coefficient (U value) |  |  |  | [W/m²K] | 2.0619 | Heat transfer coefficient (U value) |  |  |  | [W/m²K] | 0.31131
| Calculation of Uvalue for external roof before renovation (R2) | [5 empty] | Calculation of Uvalue for external roof after renovation (R2)
| Layers |  | Thickness | Thermal conductivity |  | Thermal resistance | Layers |  | Thickness | Thermal conductivity |  | Thermal resistance
|  |  | [m] | [W/mK] |  | [m²K/W] |  |  | [m] | [W/mK] |  | [m²K/W]
| 1 | [5 empty] | 1
| 2 | [5 empty] | 2
| 3 | [5 empty] | 3
| 4 | [5 empty] | 4
| 5 | [5 empty] | 5
| 6 | [5 empty] | 6
| Total |  | 0 |  |  | 0 | Total |  | 0 |  |  | 0
| Thermal resistance of interior surface |  |  | Rint | [m²K/W] |  | Thermal resistance of interior surface |  |  | Rint | [m²K/W] | 0
| Thermal resistance of exterior surface |  |  | Rext | [m²K/W] |  | Thermal resistance of exterior surface |  |  | Rext | [m²K/W] | 0
| Heat transfer coefficient (U value) |  |  |  | [W/m²K] | #DIV/0! | Heat transfer coefficient (U value) |  |  |  | [W/m²K] | #DIV/0!
| Calculation of Uvalue for external floor before renovation (F1) | [5 empty] | Calculation of Uvalue for external floor after renovation (F1)
| Layers |  | Thickness | Thermal conductivity |  | Thermal resistance | Layers |  | Thickness | Thermal conductivity |  | Thermal resistance
|  |  | [m] | [W/mK] |  | [m²K/W] |  |  | [m] | [W/mK] |  | [m²K/W]
| 1 | Concrete hollow panels | 0.22 | 1.295 |  | 0.16988 | 1 | Concrete hollow panels | 0.22 | 1.295 |  | 0.16988
| 2 | Concrete/sand mix | 0.05 | 0.76 |  | 0.065789 | 2 | Concrete/sand mix | 0.05 | 0.76 |  | 0.065789
| 3 |  |  |  |  | 0 | 3
4
| 4 | [5 empty] | 5 | [5 empty] | Gidro-bugʻ izolyatsiyasi (Ustki)
| 5 | [5 empty] | 6
| 6 | [5 empty] | 7
| Total |  | 0.27 |  |  | 0.23567 | Total |  | 0.27 |  |  | 0.23567
| Thermal resistance of interior surface |  |  | Rint | [m²K/W] | 2.1 | Thermal resistance of interior surface |  |  | Rint | [m²K/W] | 2.1
| Thermal resistance of exterior surface |  |  | Rext | [m²K/W] | 0 | Thermal resistance of exterior surface |  |  | Rext | [m²K/W] | 0
| Heat transfer coefficient (U value) |  |  |  | [W/m²K] | 0.42814 | Heat transfer coefficient (U value) |  |  |  | [W/m²K] | 0.42814
| Calculation of Uvalue for external floor before renovation (F2) | [5 empty] | Calculation of Uvalue for external floor after renovation (F2)
| Layers |  | Thickness | Thermal conductivity |  | Thermal resistance | Layers |  | Thickness | Thermal conductivity |  | Thermal resistance
|  |  | [m] | [W/mK] |  | [m²K/W] |  |  | [m] | [W/mK] |  | [m²K/W]
| 1 | [5 empty] | 1
| 2 | [5 empty] | 2
| 3 | [5 empty] | 3
| 4 | [5 empty] | 4
| 5 | [5 empty] | 5
| 6 | [5 empty] | 6
| Total |  | 0 |  |  | 0 | Total |  | 0 |  |  | 0
| Thermal resistance of interior surface |  |  | Rint | [m²K/W] |  | Thermal resistance of interior surface |  |  | Rint | [m²K/W]
| Thermal resistance of exterior surface |  |  | Rext | [m²K/W] |  | Thermal resistance of exterior surface |  |  | Rext | [m²K/W]
| Heat transfer coefficient (U value) |  |  |  | [W/m²K] | #DIV/0! | Heat transfer coefficient (U value) |  |  |  | [W/m²K] | #DIV/0!
R1
R2
R3
R4

## Losses env. before
Cumulative annual heat losses before renovation through building envelope
Element | In contact with | Wall type | Area | U value | Qtot
|  |  | [m²] | [W/m²K] | [kWh/y]
Walls | Environment |  |  |  | 0
|  | W1 | 1492.9 | 1.3755 | 95776.5591
|  | Socle 1. (heated space) | 0 | 1.8504 | 0
| Ground | Socle 2 | 0 | 0.40593 | 0
| Total annual heat losses through walls |  |  |  | 95776.5591
Roof | Environment | R2 | 0 | #DIV/0!
Semi-closed un-heated space
| Closed un-heated space | R1 | 1279.175 | 2.0619 | 123019.0423
| Total annual heat losses through roof |  |  |  | 123019.0423
Floor | Ground |  |  |  | 0
| Closed un-heated basement | F1 | 1279.175 | 0.42814 | 14809.5053
| In contact with environment | F2 | 0
| Total annual heat losses through floor |  |  |  | 14809.5053
Windows and Doors |  | Win1 | 0 | 2.56 | 0
|  | Win2 | 0 | 2.78 | 0
|  | Win3 | 256.62 | 2.94 | 20401.4286
0
|  | D1 | 61.43 | 3.5 | 5813.9502
|  | D2 | 0 | 4 | 0
|  | D3 | 0 | 5.88 | 0
| Total annual heat losses through windows and doors |  |  |  | 26215.3788
Total annual heat losses through building envelope |  |  |  |  | 259820.4855
Monthly heat losses before renovation through building envelope | [9 empty] | Heating season monthly data for Hospitals placed in II Climatic zone
[11 empty] | 13.8 | 8.5 | 3.5 | 1.9 | 3.9 | 9.4 | 15.5
[10 empty] | Month | Oct | Nov | Dec | Jan | Feb | Mar | Apr
[10 empty] | Average temp [°C] | 12,4 | 6,6 | 1,2 | -0,1 | 2,5 | 8,6 | 15,3
[10 empty] | Duration [days] | 15 | 27 | 28 | 28 | 25 | 28 | 12
|  |  | N | O | P | Q Jan | R | S | T | Δt [°C] | 9.6 | 15.4 | 20.8 | 22.1 | 19.5 | 13.4 | 6.7
Element | In contact with | Wall type | Q Oct | Q Nov | Q Dec | Q Jan | Q Feb | Q Mar | Q Apr | Duration [h] | 150 | 270 | 280 | 280 | 250 | 280 | 120
|  |  | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month]
Walls | Environment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Month | Oct | Nov | Dec | Jan | Feb | Mar | Apr
|  | W1 | 2956.9286 | 8538.1312 | 11959.1333 | 12706.5792 | 10010.4353 | 7704.4417 | 1650.9518 | Average temp [°C] | 12,4 | 6,6 | 1,2 | -0,1 | 2,5 | 8,6 | 15,3
|  | W1 | 689.95 | 5743.8337 | 10303.2533 | 11349.6775 | 8265.026 | 4346.685 | -448.4675 | Duration [days] | 15 | 27 | 28 | 28 | 25 | 28 | 12
|  | Socle 1. (heated space) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Δt [°C] | 1.6 | 7.4 | 12.8 | 14.1 | 11.5 | 5.4 | -1.3
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Duration [h] | 210 | 378 | 392 | 392 | 350 | 392 | 168
| Ground | Socle 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closed un-heated space | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total monthly heat losses through walls |  | 3646.8786 | 14281.965 | 22262.3866 | 24056.2566 | 18275.4613 | 12051.1267 | 1202.4843
Roof | Environment | R2
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Semi-closed un-heated space | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| Closed un-heated space |  | 886.1979 | 7377.5977 | 13233.8891 | 14577.9559 | 10615.9127 | 5583.0469 | -576.0287
|  | R1 | 3797.9911 | 10966.6994 | 15360.7641 | 16320.8118 | 12857.7824 | 9895.8769 | 2120.545
| Total monthly heat losses through roof |  | 4684.189 | 18344.2971 | 28594.6531 | 30898.7677 | 23473.6951 | 15478.9238 | 1544.5164
Floor | Ground |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closed un-heated basement | F1 | 788.6427 | 2277.2058 | 3189.6216 | 3388.973 | 2669.8842 | 2054.8524 | 440.3255
| In contact with environment | F2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total monthly heat losses through floor |  | 788.6427 | 2277.2058 | 3189.6216 | 3388.973 | 2669.8842 | 2054.8524 | 440.3255
Windows and Doors |  | Win1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Win2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Win3 | 1086.4264 | 3137.0563 | 4393.9913 | 4668.6158 | 3678.0062 | 2830.7444 | 606.5881
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | D1 | 309.6072 | 893.9908 | 1252.1891 | 1330.4509 | 1048.1494 | 806.6988 | 172.864
|  | D2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | D3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total monthly heat losses through openings |  | 1396.0336 | 4031.0471 | 5646.1805 | 5999.0667 | 4726.1555 | 3637.4432 | 779.4521
Total monthly heat losses through building envelope |  |  | 10515.744 | 38934.515 | 59692.8419 | 64343.0641 | 49145.1961 | 33222.346 | 3966.7783

## Losses env. after
Cumulative annual heat losses after renovation through building envelope
Element | In contact with | Wall type | Area | U value | Qtot
|  |  | [m²] | [W/m²K] | [kWh/y]
Walls | Environment |  |  |  | 0
|  | W1 | 1492.9 | 0.29459 | 20512.7097
|  | Socle 1. (heated space) | 0 | 0.31426 | 0
| Ground | Socle 2 | 0 | 0.19588 | 0
| Closed un-heated space |  |  |  | 0
| Total annual heat losses through walls |  |  |  | 20512.7097
Roof | Environment | R2 | 0
0
| Semi-closed un-heated space |  |  |  | 0
| Closed un-heated space | R1 | 1279.175 | 0.31131 | 18573.7215
| Total annual heat losses through roof |  |  |  | 18573.7215
Floor | Ground |  |  |  | 0
| Closed un-heated basement | F1 | 1279.175 | 0.42814 | 14809.5053
| In contact with environment | F2 | 0
| Total annual heat losses through floor |  |  |  | 14809.5053
Windows and Doors |  | Win4 | 256.62 | 1.5 | 10408.8921
0
|  | D4 | 61.43 | 1.8 | 2990.0315
| Total annual heat losses through windows and doors |  |  |  | 13398.9237
Total annual heat losses through building envelope |  |  |  |  | 67294.8602
Monthly heat losses before renovation through building envelope | [10 empty] | Heating season monthly data for Hospitals placed in II Climatic zone
[11 empty] | Month | Oct | Nov | Dec | Jan | Feb | Mar | Apr
[11 empty] | Average temp [°C] | 12,4 | 6,6 | 1,2 | -0,1 | 2,5 | 8,6 | 15,3
[11 empty] | Duration [days] | 15 | 27 | 28 | 28 | 25 | 28 | 12
|  |  | N | O | P | Q Jan | R | S | T |  | Δt [°C] | 9.6 | 15.4 | 20.8 | 22.1 | 19.5 | 13.4 | 6.7
Element | In contact with | Wall type | Q Oct | Q Nov | Q Dec | Q Jan | Q Feb | Q Mar | Q Apr |  | Duration [h] | 150 | 270 | 280 | 280 | 250 | 280 | 120
|  |  | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month]
Walls | Environment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Month | Oct | Nov | Dec | Jan | Feb | Mar | Apr
|  | W1 | 633.2929 | 1828.6333 | 2561.3181 | 2721.4004 | 2143.9604 | 1650.0799 | 353.5886 |  | Average temp [°C] | 12,4 | 6,6 | 1,2 | -0,1 | 2,5 | 8,6 | 15,3
|  | 0 | 147.7683 | 1230.1715 | 2206.674 | 2430.7893 | 1770.1417 | 930.9406 | -96.0494 |  | Duration [days] | 15 | 27 | 28 | 28 | 25 | 28 | 12
|  | Socle 1. (heated space) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Δt [°C] | 1.6 | 7.4 | 12.8 | 14.1 | 11.5 | 5.4 | -1.3
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Duration [h] | 210 | 378 | 392 | 392 | 350 | 392 | 168
| Ground | Socle 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closed un-heated space | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total monthly heat losses through walls |  | 781.0613 | 3058.8048 | 4767.9921 | 5152.1898 | 3914.1021 | 2581.0205 | 257.5391
Roof | Environment | R2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Semi-closed un-heated space | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closed un-heated space | 0 | 133.8004 | 1113.8881 | 1998.0855 | 2201.0161 | 1602.8169 | 842.9423 | -86.9702
|  | R1 | 573.4302 | 1655.7796 | 2319.2064 | 2464.1568 | 1941.3 | 1494.1041 | 320.1652
| Total monthly heat losses through roof |  | 707.2305 | 2769.6677 | 4317.292 | 4665.1729 | 3544.117 | 2337.0465 | 233.1949
Floor | Ground | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closed un-heated basement | F1 | 788.6427 | 2277.2058 | 3189.6216 | 3388.973 | 2669.8842 | 2054.8524 | 440.3255
| In contact with environment | F2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total monthly heat losses through floor |  | 788.6427 | 2277.2058 | 3189.6216 | 3388.973 | 2669.8842 | 2054.8524 | 440.3255
Windows and Doors |  | Win4 | 554.2992 | 1600.5389 | 2241.8323 | 2381.9468 | 1876.5338 | 1444.2574 | 309.4837
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | D4 | 159.2266 | 459.7667 | 643.983 | 684.2319 | 539.0482 | 414.8736 | 88.9015
| Total monthly heat losses through openings |  | 713.5258 | 2060.3056 | 2885.8153 | 3066.1788 | 2415.582 | 1859.131 | 398.3852
Total monthly heat losses through building envelope |  |  | 2990.4603 | 10165.984 | 15160.721 | 16272.5145 | 12543.6853 | 8832.0504 | 1329.4448
CAPEX
[10 empty] | Measure | Description of works | Type | Unit cost [USD] | Units | Total Investment [USD]
[10 empty] | Thermal insulation of walls | Thermal insulation of external walls with MW of 100mm, density of at least 120kg/m³, λ max of 0.038 [W/(m∙K)] starting from 0.3m above the ground. | W1, W2 | 51 | 1492.9 | 76137.9
[11 empty] | For socle part of the wall thermal insulation with XPS of 150mm, λ max of 0.035 [W/(m∙K)] starting from underground -0.7m up to 0.3m above the ground. Above insulation applied waterproofing layer. Visible part of socle covered with granite or decorative stone glued with metal mesh. | Socle 1 |  | 104.015 | 0
[12 empty] | Socle 2 | 174 | 0 | 0
[10 empty] | Total for walls insulation | Heating season monthly data for Hospitals placed in II Climatic zone Jan: 76137.9
[10 empty] | Thermal insulation of the roof | Heating season monthly data for Hospitals placed in II Climatic zone Month: Thermal insulation of the flat roof in contact with environment performed by removal of old layers, application of anticondens membrane, MW of 150mm thick and λ of MW 0.038 [W/(m∙K)], breathable membrane, concrete screw of 50mm thick with reinforce mesh, levelled to a smooth surface with angles for water drainage, rehabilitation of gatters, roof perimeter parapet, vent shafts and other, covered with PVC membrane of at least 2mm thick. Thermal insulation of the attic floor performed by removal of old layers, application of anticondens membrane, MW of 150mm thick and λ of MW 0.038 [W/(m∙K)], breathable membrane, concrete screw of 50mm thick with reinforce mesh. Flat roof above the attic cleaned, levelled to a smooth surface with angles for water drainage, rehabilitation of gatters, roof perimeter parapet, vent shafts and other, application of PVC membrane of at least 2mm thick; Heating season monthly data for Hospitals placed in II Climatic zone Oct: R2; Heating season monthly data for Hospitals placed in II Climatic zone Dec: 0; Heating season monthly data for Hospitals placed in II Climatic zone Jan: 0
[12 empty] | R1 | 12 | 1279.175 | 15350.1
[10 empty] | Total for roof insulation | Heating season monthly data for Hospitals placed in II Climatic zone Jan: 15350.1
[10 empty] | Thermal insulation of floors | Basement ceiling and floors in contact with environment insulation with 150 mm of MW with a thermal conductivity of λ = 0.038 W / (mK) by gluing and fixing with dowels the MW boards to the basement ceiling, covering MW boards with mesh and plaster, application of white paint for asthetic view of surface. | F1, F2 | 9 | 1279.175 | 11512.575
[10 empty] | Replacement of windows and doors | Replacing the existing openings with PVC framed, 5 camera, double glazed [4mm (Low-e < 0.1) - 20 Ar - 4mm] with maximum Uvalue for windows of 1.5 [W/m²K] and for doors 1.8 [W/m²K] with U shape metal reinforcement of at least 1.5mm. Doors to be equipped with automatic closing devices and aluminium dorstep. Vapor barrier membrane applied on the perimeter of PVC frame from inside and breathable membrane from outside. Insulation of perimeter of openings from inside and outside with high density MW of at least 40mm thick. | Win4, D4. | 255.75 | 65 | 16623.75

## Ventilation losses
Annual heat losses through natural ventilation before and after renovation
| Name of the Building | Net heated volume | Air exchange rate | L | Q
|  | [m³] |  | [m³/h] | [kWh/y]
Before renovation | 3-DMTT | 7546.245 | 0.4 | 3018.498 | 65614.0862 |  | wooden openings | 0.5
|  |  |  | 0 | 0 |  | bad PVC | 0.4
|  |  |  | 0 | 0 |  | new PVC | 0.35
|  |  |  | 0 | 0
| Total annual heat losses through natural ventilation and infiltration |  |  |  | 65614.0862
After renovation | 3-DMTT | 7546.245 | 0.35 | 2641.1858 | 57412.3254
| 0 |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
| Total annual heat losses through natural ventilation and infiltration |  |  |  | 57412.3254
Heat savings from natural ventilation |  |  |  |  | 8201.7608
Monthly heat losses through natural ventilation before and after renovation | [12 empty] | Heating season monthly data for Hospitals placed in II Climatic zone
| Name of the Building | L | cxƔ | Conversion coeff. | Q Oct | Q Nov | Q Dec | Q Jan | Q Feb | Q Mar | Q Apr
|  | [m³/h] |  |  | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] |  | Month | Oct | Nov | Dec | Jan | Feb | Mar | Apr
Before renovation | 3-DMTT | 3018.498 | 0.288 | 1.163 | 3494.1121 | 10089.2486 | 14131.7421 | 15014.976 | 11829.0252 | 9104.1031 | 1950.8792 |  | Average temp [°C] | 12,4 | 6,6 | 1,2 | -0,1 | 2,5 | 8,6 | 15,3
| 0 | 0 | 0.288 | 1.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Duration [days] | 15 | 27 | 28 | 28 | 25 | 28 | 12
|  | 0 | 0.288 | 1.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Δt [°C] | 9.6 | 15.4 | 20.8 | 22.1 | 19.5 | 13.4 | 6.7
|  | 0 | 0.288 | 1.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Duration [h] | 360 | 648 | 672 | 672 | 600 | 672 | 288
| Total monthly heat losses through natural ventilation and infiltration |  |  |  | 3494.1121 | 10089.2486 | 14131.7421 | 15014.976 | 11829.0252 | 9104.1031 | 1950.8792
After renovation | 3-DMTT | 2641.1858 | 0.288 | 1.163 | 3057.348 | 8828.0925 | 12365.2743 | 13138.104 | 10350.397 | 7966.0902 | 1707.0193
| 0 | 0 | 0.288 | 1.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0.288 | 1.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0.288 | 1.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total monthly heat losses through natural ventilation and infiltration |  |  |  | 3057.348 | 8828.0925 | 12365.2743 | 13138.104 | 10350.397 | 7966.0902 | 1707.0193
Monthly heat savings from natural ventilation |  |  |  |  | 436.764 | 1261.1561 | 1766.4678 | 1876.872 | 1478.6281 | 1138.0129 | 243.8599
Annual heat losses through mechanical ventilation before and after renovation
| Block/floor name | Unit description | No of people | Fresh air per person | VSUPPLY &/OR EXAHUST [m³/h] | Heat recovery efficiency [%] | Q [kWh/y]
[m³/h/person]
Before renovation | 3-DMTT | Mavjud egzoz ventilyatori | 418 | 20 | 8360 | 0% | 75718.3651
0
[6 empty] | 0% | 0
[6 empty] | 0% | 0
0
| Annual heat losses through mechanical ventilation before renovation | [5 empty] | 75718.3651
| Annual electrical energy consumption for mechanical ventilation before renovation | [5 empty] | 0
After renovation | 3-DMTT | [5 empty] | 0
| 0 | AHU's with heat recovery | 418 | 20 | 8360 | 85% | 11357.7548
| 0 | 0 |  |  | 0 | 0% | 0
| 0 | 0 |  |  | 0 | 0% | 0
| Annual heat losses through mechanical ventilation after renovation | [5 empty] | 11357.7548
| Annual electrical energy consumption for mechanical ventilation after renovation | [5 empty] | 3424.256
Annual electrical energy savings from mechanical ventilation | [6 empty] | -3424.256
Annual heat savings from mechanical ventilation | [6 empty] | 64360.6103
Note: Fresh air per person of 80m3/h is assumed as an average value per hospital considered during the EA calculation. During the design phase, spaces as: surgery rooms, clean rooms, intensive care, x-ray etc. will be calculated separately according to the specific technological requirements.
20-30
Monthly heat losses through mechanical ventilation before and after renovation
| Block/floor name | Unit description | VSUPPLY &/OR EXAHUST [m³/h] | cxƔ | Conversion coeff. | Heat recovery efficiency [%] | Utilization factor | Q Oct | Q Nov | Q Dec | Q Jan | Q Feb | Month: Q Mar; Oct: Q Apr
[8 empty] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] | Month: [kWh/month]; Oct: [kWh/month]
Before renovation | 3-DMTT | Mavjud egzoz ventilyatori | 8360 | 0.288 | 1.163 | 0% | 0.41667 | 4032.1898 | 11642.9482 | 16307.9678 | 17327.2158 | 13650.6427 | Month: 10506.0947; Oct: 2251.306
| 0 | 0 | 0 | 0.288 | 1.163 | 0% | 0.5 | 0 | 0 | 0 | 0 | 0 | Month: 0; Oct: 0
| 0 | 0 | 0 | 0.288 | 1.163 | 0% | 0.125 | 0 | 0 | 0 | 0 | 0 | Month: 0; Oct: 0
| 0 | 0 | 0 | 0.288 | 1.163 | 0% | 0.125 | 0 | 0 | 0 | 0 | 0 | Month: 0; Oct: 0
| 0 | 0 | 0 | 0.288 | 1.163 | 0% | 1 | 0 | 0 | 0 | 0 | 0 | Month: 0; Oct: 0
| Monthly heat losses through mechanical ventilation before renovation | [6 empty] | 4032.1898 | 11642.9482 | 16307.9678 | 17327.2158 | 13650.6427 | Month: 10506.0947; Oct: 2251.306
After renovation | 3-DMTT | 0 | 0 | 0.288 | 1.163 | 0% | 0.41667 | 0 | 0 | 0 | 0 | 0 | Month: 0; Oct: 0
| 0 | AHU's with heat recovery | 8360 | 0.288 | 1.163 | 85% | 0.41667 | 604.8285 | 1746.4422 | 2446.1952 | 2599.0824 | 2047.5964 | Month: 1575.9142; Oct: 337.6959
| 0 | 0 | 0 | 0.288 | 1.163 | 0% | 0.125 | 0 | 0 | 0 | 0 | 0 | Month: 0; Oct: 0
| 0 | 0 | 0 | 0.288 | 1.163 | 0% | 0.125 | 0 | 0 | 0 | 0 | 0 | Month: 0; Oct: 0
| 0 | 0 | 0 | 0.288 | 1.163 | 0% | 0.1 | 0 | 0 | 0 | 0 | 0 | Month: 0; Oct: 0
| Monthly heat losses through mechanical ventilation after renovation | [6 empty] | 604.8285 | 1746.4422 | 2446.1952 | 2599.0824 | 2047.5964 | Month: 1575.9142; Oct: 337.6959
Monthly heat savings from mechanical ventilation | [7 empty] | 3427.3614 | 9896.506 | 13861.7727 | 14728.1335 | 11603.0463 | Month: 8930.1805; Oct: 1913.6101
CAPEX
|  | Measure | Description | Cost [USD/m³] | units | Total Investment [USD]
|  | Mechanical ventilation with heat recovery | Wallmounted AHU units with heat recover 85% | 850 | 41.8 | 20139
Note:The cost is assumed in average per 1m³ of heated volume of already rehabilitated hospitals, with updated market prices from Q3 of 2022.
Note on E10: Saidmurodjon Khamdamov: E10=0,35

## Heat gains Mec Vent
Annual heat gains from mechanical ventilation before and after renovation
| Block/floor name | Unit description | No of people | Fresh air per person [m³/h/person] | VSUPPLY &/OR EXAHUST * [m³/h] | ρ [kg/m³] | Conversion coeff. | ΔI [kJ/kg] | Operation hours during cooling season [h/y] | Heat exchanger efficiency | Q
[10 empty] | [%] | [kWh/y]
Before renovation | 3-DMTT | Mavjud egzoz ventilyatori |  |  | 8360 | 1.2 | 0.27778 | 11.1 | 0 | 0% | 0
[6 empty] | 1.2 | 0.27778 | 11.1 |  | 0% | 0
[6 empty] | 1.2 | 0.27778 | 11.1 |  | 0% | 0
[6 empty] | 1.2 | 0.27778 | 11.1 |  | 0% | 0
| 0 |  | 0 | 0 | 0 | 1.2 | 0.27778 | 11.1 |  | 0% | 0
| Total heat gains through mechanical ventilation before renovation | [9 empty] | 0
After renovation | 3-DMTT | Mavjud egzoz ventilyatori |  | 0 | 8360 | 1.2 | 0.27778 | 11.1 | 0 | 0% | 0
|  | AHU's with heat recovery | 418 | 20 | 8360 | 1.2 | 0.27778 | 11.1 | 720 | 85% | 3340.6587
|  | 0 | 0 | 0 |  | 1.2 | 0.27778 | 11.1 | 0 | 0% | 0
|  | 0 | 0 | 0 |  | 1.2 | 0.27778 | 11.1 | 0 | 0% | 0
|  |  |  | 0 | 0 | 1.2 | 0.27778 | 11.1 | 0 | 0% | 0
| Total heat gains through mechanical ventilation after renovation | [9 empty] | 3340.6587
Cooling energy savings from mechanical ventilation | [10 empty] | -3340.6587
* - If some figure is dominating for supply or exhaust in the same space, please apply the maximum value. Please avoid double counting in case if 2 units serve same space (for ex. kitchen 1 supply fan of 800m3/h and 1 exhaust fan of 1000m3/h, only exhaust fan for 1000m3/h should be considered during cooling energy loss calculation. Cooling energy losses are calculated only for air conditioned spaces.

## gains
Before renovation
Windows | [10 empty] | Table A.4, page 126, Solar radiation, kWh/m2
| Area, m2 | gn | Fw | Fhor | Fov | Ffin | Fsh | Asol, m2 | Fsh*Asol, m2 |  | Month | South | North | East, West | South-east, south-west | North-east, north-west | Horizontal
South | 79.02 | 0.75 | 0.6 | 0.85 | 0.9 | 0.94 | 0.7191 | 24.8913 | 17.8993 |  | January | 65 | 17.7 | 28.5 | 51.2 | 18.7 | 33.5
North | 86.4 | 0.75 | 0.6 | 0.98 | 0.91 | 1 | 0.8918 | 27.216 | 24.2712 |  | February | 76.3 | 21.9 | 38.9 | 62.3 | 24.4 | 49.8
East, West | 25.56 | 0.75 | 0.6 | 0.82 | 0.89 | 0.92 | 0.67142 | 8.0514 | 5.4058 |  | March | 96 | 29.3 | 61.3 | 85 | 37.5 | 91.5
South-east, south-west | 0 | 0.75 | 0.6 | 0.82 | 0.89 | 0.92 | 0.67142 | 0 | 0 |  | April | 20.1 | 7.9 | 16.7 | 20.1 | 11.6 | 28.3
North-east, north-west | 0 | 0.75 | 0.6 | 0.82 | 0.89 | 0.92 | 0.67142 | 0 | 0 |  | October | 24.3 | 5.8 | 12.7 | 20.3 | 7 | 19.9
Horizontal |  | 0.75 | 0.6 | 1 | 1 | 1 | 1 | 0 | 0 |  | November | 60.8 | 13.1 | 24 | 48 | 14.3 | 37.5
[11 empty] | December | 58.4 | 11.5 | 20 | 44.5 | 11.7 | 26.7
Month | Heating days | Outdoor air temperature, oC | Specific internal heat gains, kWh/m2 | Internal heat gains, kWh | Solar heat gains, kWh | Total heat gains, kWh | Total heat losses, kWh | gains/losses | Heat gain utilization factor | Energy need for space heating, kWh | Total | 400.9 | 107.2 | 202.1 | 331.4 | 125.2 | 287.2 | Measured data. kWh
January | 28 | -0,1 | 4.032 | 10142.1533 | 1747.1239 | 11889.2771 | 96685.2559 | 0.12297 | 0.99987 | 84797.5467 | [7 empty] | 63146.5 | 1.3429
February | 24 | 2,5 | 3.456 | 8693.2742 | 2107.5462 | 10800.8205 | 74624.864 | 0.14473 | 0.99975 | 63826.7977 | Table 10, page 100 | [6 empty] | 52177.1667 | 1.2233
March | 28 | 8,6 | 4.032 | 10142.1533 | 2760.861 | 12903.0142 | 52832.5438 | 0.24422 | 0.99797 | 39955.7165 | Internal heat gains | 6 | W/m2 |  |  |  |  | 25070.5 | 1.5937
April | 15 | 15,3 | 2.16 | 5433.2964 | 641.7968 | 6075.0932 | 8168.9635 | 0.74368 | 0.90594 | 2665.284 | [7 empty] | 3920.3333 | 0.67986
October | 14 | 12,4 | 2.016 | 5071.0766 | 644.3811 | 5715.4577 | 18042.0459 | 0.31679 | 0.99452 | 12357.9155 | Table 11, page 102 | [6 empty] | 7172.5 | 1.723
November | 26 | 6,6 | 3.744 | 9417.7138 | 1535.9727 | 10953.6865 | 60666.7118 | 0.18056 | 0.99938 | 49719.8002 | Type of window | gn | [5 empty] | 24503.6667 | 2.0291
December | 28 | 1,2 | 4.032 | 10142.1533 | 1432.557 | 11574.7103 | 90132.5518 | 0.12842 | 0.99984 | 78559.6615 | One glass pane | 0.85 | [5 empty] | 46486.6667 | 1.6899
Total | 163 | 0 | 23.472 | 59041.8209 | 10870.2387 | 69912.0596 | 401152.9367 | 0.17428 |  | 331882.7221 | Double glass panes, double window | 0.75 | [5 empty] | 222477.3333 | 1.4918
[11 empty] | Double window with selective coating low-e | 0.67
After renovation | [10 empty] | Tripple glass window | 0.7
[11 empty] | Tripple glass window wilh selective coating low-e | 0.5
Windows
| Area, m2 | gn | Fw | Fhor | Fov | Ffin | Fsh | Asol, m2 | Fsh*Asol, m2
South | 79.02 | 0.7 | 0.9 | 0.85 | 0.9 | 0.94 | 0.7191 | 34.8478 | 25.0591
North | 86.4 | 0.7 | 0.9 | 0.98 | 0.91 | 1 | 0.8918 | 38.1024 | 33.9797
East, West | 25.56 | 0.7 | 0.9 | 0.82 | 0.89 | 0.92 | 0.67142 | 11.272 | 7.5682
South-east, south-west | 0 | 0.7 | 0.9 | 0.82 | 0.89 | 0.92 | 0.67142 | 0 | 0
North-east, north-west | 0 | 0.7 | 0.9 | 0.82 | 0.89 | 0.92 | 0.67142 | 0 | 0
Horizontal | 0 | 0.7 | 0.9 | 1 | 1 | 1 | 1 | 0 | 0
Month | Heating days | Outdoor air temperature, oC | Specific internal heat gains, kWh/m2 | Internal heat gains, kWh | Solar heat gains, kWh | Total heat gains, kWh | Total heat losses, kWh | gains/losses | Heat gain utilization factor | Energy need for space heating, kWh
January | 28 | -3.5 | 4.032 | 10142.1533 | 2445.9734 | 12588.1267 | 32009.7008 | 0.39326 | 0.99427 | 19493.68
February | 24 | -2.5 | 3.456 | 8693.2742 | 2950.5647 | 11643.8389 | 24941.6787 | 0.46684 | 0.98805 | 13436.9386
March | 28 | 2.6 | 4.032 | 10142.1533 | 3865.2054 | 14007.3586 | 18374.0548 | 0.76234 | 0.92386 | 5433.2022
April | 15 | 7.2 | 2.16 | 5433.2964 | 898.5156 | 6331.812 | 3374.16 | 1.8766 | 0.52194 | 69.3161
October | 14 | 7.3 | 2.016 | 5071.0766 | 902.1335 | 5973.2102 | 6652.6368 | 0.89787 | 0.87481 | 1427.1954
November | 26 | 3.9 | 3.744 | 9417.7138 | 2150.3618 | 11568.0756 | 20740.5187 | 0.55775 | 0.97539 | 9457.1577
December | 28 | -0.9 | 4.032 | 10142.1533 | 2005.5798 | 12147.7331 | 29972.1905 | 0.4053 | 0.99347 | 17903.8182
Total | 163 | 1.2344 | 23.472 | 59041.8209 | 15218.3341 | 74260.155 | 136064.9403 | 0.54577 |  | 67221.3082
Note on C4: table 11, page 102
Note on D4: 0.9 = Fw (formula 36, page 102)
Note on E4: Table 12, page 103
Note on F4: Tabke 13, page 104
Note on G4: Table 14, page 104
Note on I12: Formula 41, page 105
Note on J12: Formula 38, page 105
Note on C25: table 11, page 102
Note on D25: 0.9 = Fw (formula 36, page 102)
Note on E25: Table 12, page 103
Note on F25: Tabke 13, page 104
Note on G25: Table 14, page 104
Note on I33: Formula 41, page 105
Note on J33: Formula 38, page 105

## Heat distr. efficiency
Heat distribution losses inside basement
| Building name | Interior nominal diameter of pipe (DN), [mm] | Length [m] | Percentage of insulated pipes | Length of insulated pipes [m] | Length of non-insulated pipes [m] | Losses through non-insulated pipes [W/m] | Losses through insulated pipes [W/m] | Hours per year [h/y] | Q [kWh/y]
Pierderea maximă a densităţii fluxului de căldură prin țevi izolate în spații neîncălzite, [W/m]
[13 empty] | Diametrul nominal interior al conductei (DN), [mm] | Temperatura medie a agentului termic, [°C]
Before renovation | [9 empty] | 0 | [9 empty] | Month | Oct | Nov | Dec | Jan | Feb | Mar | Apr
[10 empty] | 0 | [9 empty] | Average temp [°C] | 12,4 | 6,6 | 1,2 | -0,1 | 2,5 | 8,6 | 15,3
[10 empty] | 0 |  |  |  | ≤50 | 60 | 70 | 80 | ≥90 |  | Duration [days] | 15 | 27 | 28 | 28 | 25 | 28 | 12
| 3-DMTT | [8 empty] | 0 |  |  | 15 – 25 | 7 | 11 | 13 | 14 | 16 |  | Δt [°C] | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  | 15 – 25 | 480 | 0% | 0 | 480 | 47 | 11 | 1630 | 36772.8 |  |  | 32 – 50 | 10 | 14 | 16 | 18 | 21 |  | Duration [h] | 150 | 270 | 280 | 280 | 250 | 280 | 120
[10 empty] | 0 |  |  | 65 – 100 | 14 | 19 | 22 | 25 | 29
| Total heat losses through heat distribution system before renovation | [8 empty] | 36772.8 | [9 empty] | Month | Oct | Nov | Dec | Jan | Feb | Mar | Apr
After renovation | [9 empty] | 0 | 372 | [8 empty] | Average temp [°C] | 12,4 | 6,6 | 1,2 | -0,1 | 2,5 | 8,6 | 15,3
[10 empty] | 0 | 64 |  | Pierderea maximă a densității fluxului de căldură prin țevi neizolate în spații neîncălzite, [W/m] | [6 empty] | Duration [days] | 15 | 27 | 28 | 28 | 25 | 28 | 12
[10 empty] | 0 | 152 |  | Diametrul nominal interior al conductei (DN), [mm] | Temperatura medie a agentului termic – 60[°C] | [5 empty] | Δt [°C] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 3-DMTT | [8 empty] | 0 | [9 empty] | Duration [h] | 210 | 378 | 392 | 392 | 350 | 392 | 168
|  | 15 – 25 | 480 | 100% | 480 | 0 | 47 | 11 | 1630 | 8606.4 |  |  | 15 – 25 | 47
[10 empty] | 0 |  |  | 32 – 50 | 74
| Total heat losses through heat distribution system after renovation | [8 empty] | 8606.4 |  |  | 65 – 100 | 140 | [5 empty] | Element | Type |  | Q Oct | Q Nov | Q Dec | Q Jan | Q Feb | Q Mar | Q Apr
Heat savings from heat distribution system | [9 empty] | 28166.4 | [12 empty] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month] | [kWh/month]
Chugun (ish vaqti)
Costs to be applied in CAPEX
[14 empty] | Diameter | Pipe price [USD/m] | Fitings [USD] | Insulation price [USD/m] | Labour [USD] | Total [USD/m]
| Building name | Radiator turi | Soni | A (m²) | Jami (m²) | K (W/m²K) | Q [kWh/y] | [6 empty] | 15 – 25 | 3 | 1.5 | 2 | 2.1667 | 8.6667
[14 empty] | 32 – 50 | 7 | 3.5 | 4 | 4.8333 | 19.3333
[14 empty] | 65 – 100 | 24 | 12 | 10 | 15.3333 | 61.3333
Before renovation | 3-DMTT | Chugun | 10 | 1.2 | 12 | 9
CAPEX
[13 empty] | Unit cost [USD] | Units
| Radiatorlarni almashtirish (15% samaradorlik) | [10 empty] | Bimetal radiators with an average dimension of 500x800mm equiped with antivandal type mechanical thermostatic valve, fitings and labour.
After renovation | [11 empty] | Bitubular distribution of PP-RCT/PP-RCT+BF/PP-RCT pipe insulated with expended polyethene with a thickness of at least 25mm including fitings.
Labour for uninstall the old system and install the new one.
[12 empty] | Heating system replacement |  |  | 18000
in case of external networks, using pipes 65-100mm: 1. to replace the description with: Steel electric welved pipe, placed in concrete channels at 1m depth in the ground, treated with anticorrosion, insulated with high density MW of at least 40mm covered with aluminum foil including fitings and labour. Asphalt or tile rehabilitaiton included. 2. to replace unit price of 61 USD/m2 with 340 USD/m2
Heat savings from heat distribution system

## DHW generation
Before implementation
Descriotion of source | Energy used for DHW preparation | Consumption [litres/person * day] | No of persons | During heating season |  | Outside heating season |  | Conversion coeff. | Q [kWh/y] | Electrical energy
|  |  |  | ΔT [°C] | Working days [days/y] | ΔT [°C] | Working days [days/y] |  |  | Other energy
ARISTON | Electrical energy | 15 | 13 | 55 | 163 | 45 | 202 | 1.163 | 4094.6032
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
Total electrical energy needs for DHW preparation | [8 empty] | 4094.6032
Total other energy needs for DHW preparation | [8 empty] | 0
Total energy needs for DHW preparation | [8 empty] | 4094.6032
After implementation
Descriotion of source | Energy used for DHW preparation | Consumption [litres/person * day] | No of persons | During heating season |  | Outside heating season |  | Conversion coeff. | Q [kWh/y]
|  |  |  | ΔT [°C] | Working days [days/y] | ΔT [°C] | Working days [days/y]
ARISTON | Electrical energy | 15 | 13 | 55 | 163 | 45 | 202 | 1.163 | 4094.6032
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
|  | 15 |  | 55 | 163 | 45 | 202 | 1.163 | 0
Total electrical energy needs for DHW preparation | [8 empty] | 4094.6032
Total other energy needs for DHW preparation | [8 empty] | 0
Total energy needs for DHW preparation | [8 empty] | 4094.6032

## DHW distr. efficiency
| Building name | Interior nominal diameter of pipe (DN), [mm] | Length [m] | Percentage of insulated pipes | Length of insulated pipes [m] | Length of non-insulated pipes [m] | Losses through non-insulated pipes [W/m] | Losses through insulated pipes [W/m] | Hours per year [h/y] | Q [kWh/y]
Pierderea maximă a densităţii fluxului de căldură prin țevi izolate în spații neîncălzite, [W/m]
[14 empty] | Diametrul nominal interior al conductei (DN), [mm] | Temperatura medie a agentului termic, [°C]
Before renovation
[15 empty] | ≤50 | 60 assumed | 70 | 80 | ≥90 | 60
[14 empty] | 15 – 25 | 7 | 2.2 | 13 | 14 | 16 | 11
[14 empty] | 32 – 50 | 10 | 2.8 | 16 | 18 | 21 | 14
[14 empty] | 65 – 100 | 14 | 3.8 | 22 | 25 | 29 | 19
| Total heat losses through DHW distribution system before renovation | [8 empty] | 0
After renovation
Pierderea maximă a densității fluxului de căldură prin țevi neizolate în spații neîncălzite, [W/m]
[14 empty] | Diametrul nominal interior al conductei (DN), [mm] | Temperatura medie a agentului termic asumata – 60[°C] | Temperatura medie a agentului termic – 60[°C]
[14 empty] | 15 – 25 | 9.4 | 47
[14 empty] | 32 – 50 | 14.8 | 74
| Total heat losses through DHW distribution system after renovation | [8 empty] | 0 |  |  |  | 65 – 100 | 28 | 140
Heat savings from DHW distribution system | [9 empty] | 0
Costs to be applied in CAPEX
[14 empty] | Diameter | Pipe price [USD/m] | Fitings [USD] | Insulation price [USD/m] | Labour [USD] | Total [USD/m]
[14 empty] | 15 – 25 | 3 | 1.5 | 2 | 2.1667 | 8.6667
[14 empty] | 32 – 50 | 7 | 3.5 | 4 | 4.8333 | 19.3333
[14 empty] | 65 – 100 | 24 | 12 | 10 | 15.3333 | 61.3333
CAPEX
[11 empty] | Pipe diameter | Description | Unit cost [USD/m] | Length [m] | Total [USD]
[11 empty] | 15-25 | PP-RCT/PP-RCT+BF/PP-RCT pipe insulated with expended polyethene with a thickness of at least 20mm including fitings and labour | 15 |  | 0
[11 empty] | 32-50 | PP-RCT/PP-RCT+BF/PP-RCT pipe insulated with expended polyethene with a thickness of at least 25mm including fitings and labour | 28 |  | 0
[11 empty] | 65-100 | Steel electric welved pipe, treated with anticorrosion, insulated with high density MW of at least 40mm covered with aluminum foil including fitings and labour | 61.3333 |  | 0
[11 empty] | Labour |  |  |  | 0
[11 empty] | Other unforeseen works |  |  |  | 0
[11 empty] | DHW distribution system replacement |  |  |  | 0
in case of external networks, using pipes 65-100mm: 1. to replace the description with: Steel electric welved pipe, placed in concrete channels at 1m depth in the ground, treated with anticorrosion, insulated with high density MW of at least 40mm covered with aluminum foil including fitings and labour. Asphalt or tile rehabilitaiton included. 2. to replace unit price of 61 EUR/m2 with 340 EUR/m2

## IHS
Modernization of IHS
Individual Heat Substation with weather compensation control
Heat exchanger for heating [kW]
Heat exchanger for DHW [kW]
Heat exchanger for ventilation [kW]
Savings [kWh/y]
CAPEX for IHS with weather compensation control | EUR
Heat exchanger for heating system in prefabricated insulation | 0
Heat exchanger for DHW in prefabricated insulation | 0
Heat exchanger for ventilation in prefabricated insulation | 0
Circulation pumps, working & reserve for heating system equipped with frequency drive in prefabricated insulation | 0
Circulation pumps, working & reserve for DHW equipped with frequency drive in prefabricated insulation | 0
Circulation pumps, working & reserve for ventilation system equipped with frequency drive in prefabricated insulation | 0
Water treatment station | 0
Accessories (valves, anemometers, thermometers, insulation etc.) | 0
Automatization | 0
Labour | 0
Total | 22770

## Lighting
Annual electricity consumption for artificial lighting before and after renovation
| Name of the Building | Area [m²] | Floor ratio covered by various lighting sources |  |  |  | Average installed power per sq m including losses [W/m²] | Operation hours per year [h/y] | Utilization factor | Annual energy consumption [kWh/y] | [6 empty] | Percentage share by room types in hospital institutions
|  |  | Incandescent | Fluorescent | Fluorescent | LED | [5 empty] | Normative values for hospitals - average |  |  |  |  | Nr. | Nivel de iluminat, lx | Cota %
Before renovation | [6 empty] | 0 |  | 0.3 | 0 |  | Source | W/m2 |  |  |  | 1 | 20 | 0,1
| 3-DMTT | 2515.415 | 1% | 98% | 0% | 1% | 17.768 | 1630 | 0.55 | 40068.0757 |  | Incandescent | 25 | do not ensure 300 lx |  |  | 2 | 30 | 0,5
[7 empty] | 0 |  | 0.3 | 0 |  | Fluorescent, electromagnetic ballast, 4x18W | 17.8 |  |  |  | 3 | 50 | 1,5
[7 empty] | 0 |  | 0.3 | 0 |  | Fluorescent, electronic ballast, 4x18 | 14.81 |  |  |  | 4 | 75 | 1,75
| Total annual energy consumption for artificial lighting before renovation | [8 empty] | 40068.0757 |  | LED 600x600 mm, 37W, 3684 lm | 7.4 |  |  |  | 5 | 100 | 2,25
After renovation | [6 empty] | 0 | 0 | 0.3 | 0 | [6 empty] | 6 | 150 | 3,5
| 3-DMTT | 2515.415 | 0% | 0% | 0% | 100% | 7.4 | 1630 | 0.55 | 16687.5147 | [6 empty] | 7 | 200 | 6,4
|  | 0 |  |  |  |  | 0 | 0 | 0.3 | 0 | [6 empty] | 8 | 300 | 60
|  | 0 |  |  |  |  | 0 | 0 | 0.3 | 0 | [6 empty] | 9 | 400 | 16
| Total annual energy consumption for artificial lighting after renovation | [8 empty] | 16687.5147 | [6 empty] | 10 | 500 | 8
Electricity savings | [9 empty] | 23380.5611 | [6 empty] | Average 300 lx considered
CAPEX
| Installation of LED lighting and replacing of distribution system | [9 empty] | Specific powers of general lighting according to lighting levels for rooms in hospital institutions
| Description | Cost [USD/m²] | Surface | Total Investment [USD] | [6 empty] | N | Names of rooms | The value of lighting, Emin, lx | Area | LED | FLUO-T8 | FLUO-T8 | INCANDES,
| Instalaltion of LED lighting and replacing of interior electrical distribution system. LED lumminaires to be selected in-line with results of simulation from DIALUX for each specific space according to the destination and normative requirements. LED lighting sources placed in commonly used spaces to be equipped with presence sensors. All wiring to be replaced, including electrical cabinets, switches and plugs | 21 | 2515.415 | 30000 | [9 empty] | m2 | W/m2 | -BALAST ELECTRONIC, | -BALAST ELECTROM. W/m2 | W/m2
W/m2
[11 empty] | 1 | Delivery room, dialysis, resuscitation rooms, anesthesia, toilet for newborns; Bandage room (clean, purulent, plaster sectors); Angiography room; Offices for surgeons, obstetricians, gynecologists, traumatologists, paediatricians, specialists in infectious diseases, dermatovenerologists, allergists, dentists, examination, reception and examination boxes; Urgent analysis room, booths, serological examination rooms, colorimetric rooms, clerical laboratory; Working room for dental technicians, amalgam sector; Room for plaster, polymerisation; Rooms for epidemiologists, bacteriologists, booths for serological studies of particularly dangerous infections; | 500 | xx | 11,42 | 24,69 | 35,5 | -
Rooms for the zoo-parasitologist for the reception and analysis of material infected with dangerous infections; Procedure room, handling, blood transfusion, BCG, defibrillation, acupuncture, pneumothorax;
[11 empty] | 2 | Operating room, hypothymia room, cystoscopy; Installation chambers for cardiopulmonary bypass, artificial kidney, etc.; | 400 | xx | 9,55 | 22,0 | 26,66 | -
Intracavitary gamma-therapy cabin; The dissection-autopsy room; Rooms for entomologists, helminthologists, virologists, bacteriologists, laboratory, chemical, biochemical laboratories, serological boxes, preparation rooms; Vivarium. Rooms for keeping animals;
Procedure rooms: bacteriology, virology, toxicology; The offices of the chief physician, the deputy chief physician, the head of department;
[11 empty] | 3 | Preoperative room, room for observation during operations; Doctors' offices in outpatient clinics not listed above; Medical offices without receiving patients, staff room, training room / acquisition of methods; Occupational therapy; | 300 | xx | 7,4 | 14,8 | 17,8 | -
X-ray operating unit: X-ray operating room; X-ray computed tomography room: procedure room;
Roentgen-therapy room: procedure room; Radiometry room, dosimetry; Radiotherapy room with high energy radiation, scanner room; Preparation and general clinical, hematological and biochemical, bacteriological, histological and cytological laboratories;
Medical laboratory offices, blood sampling, cytological sampling, coagulography, photometry; Weighing room, thermostatic room, medium preparation room with medium pouring box, room for staining samples, centrifuge; Room for the repair and sharpening of surgical instruments; Rooms for the study of autopsy and biopsy material; Departments of radiology, radiochemistry, spectroscopy and polarography Rooms, acoustics laboratories, vibrations, electromagnetic fields, work physiology, can cooking, termite; Laundries;
Încăperi pentru preluarea de probe; Încăpere de preluare biotest, Încăperi pentru depozitarea mediilor nutritive, pre-box;
Dispatch room for receiving calls and directing emergency service crews; Milk filtering and bottling room; Room for the preparation of fermented dairy products and lactic acid mixtures; Rooms for the preparation and packaging of cow's cheese; Rooms for the preparation of fruits, vegetables and the preparation of fruit and vegetable mixtures, Rooms for the preparation of fish, meat and the preparation of fish and meat cuts; Offices of nurses, housewives, on-call nurse positions;
Guard post;
[11 empty] | 4 | Fotarii, rooms for electroluminotherapy, aeroionotherapy, thermotherapy, kinetherapy, massage, mechanotherapy, ultrasound, UHF; | 200 | xx | 4,7 | 10,9 | 13,0 | -
X-ray bronchoscopy and laparoscopy; The roentgen-diagnostic room, the roentgenoscopy procedure room, the generator room;
photo examination room of x-ray departments; Storage room for analyzes of patients undergoing research, extracts of solid and liquid radioactive waste; Wards of children's wards for newborns, postoperative wards, intensive care and glaucoma wards, filters and reception boxes, isolator; Rooms for receiving, issuing and recording tests, receiving and sorting samples;
Rooms with booths for duodenal sounding and gastric juice collection; Glass blowing room; Linear sector, to be glued;
Spălătorie vase; Sector sterilizare în autoclav; Încăpere pentru recepția și depozitarea materialelor sterile, depozit pentru depozitarea materialelor sterile; Încăpere pentru pregătirea instrumentelor chirurgicale pentru sterilizare; Camera de pre-secționare-autopsie, de fixare; Încăperi pentru îmbrăcarea cadavrelor, sala de înmormântare; Secții de expediere, ambalare, Încăperi pentru depozitare și distribuție de momeli gata preparate, distribuție de dezinfectanți și preparate bacteriene; Încăperi de dezinfectare, secții de spălare; Izolatoare pentru animale infecțioase, carantine; Sala preparare a bucătăriilor; Sala de posturi radio; Sala echipelor de teren;
Încăperi pentru recepția și păstrarea veselei; Camera de distribuție; Sala de control (panouri de control) in secțiile radiologice etc.;
Camere de zi, pentru conversații cu medicul, hrănirea copiilor sub 1 an, extragerea laptelui matern și sterilizarea acestuia; Registratura;
[11 empty] | 5 | Blood storage room; Functional diagnostic rooms, endoscopy rooms; Hydrotherapy, therapeutic baths, shower rooms; | 150 | xx | 3,65 | 7,41 | 8,89 | 28,5
Hall with oxygenation barochambers; procedure room for fluography; engineering room; Room for keeping: laboratory vessels;
Rooms for storing disinfection equipment and inventory, dirty and clean linen; Rooms of the current stock of medicines; Central material and linen rooms; Corridors in operating theaters, maternity wards, resuscitation and intensive care units, waiting corridors in ambulatory institutions and polyclinics; Corridors in lounge sections, main halls;
[11 empty] | 6 | Changing room area; waiting room; barium preparation booth; Condenser room; Storage of radioactive substances; | 100 | xx | 2,5 | 5,9 | 4,9 | 20,5
Lounges of psychiatric wards; Other lounges and bedrooms for mothers; Room for keeping: reagents; Storage rooms for biological, medical and diagnostic products, reagents, disinfectants, acids; Storage rooms for mobile team boxes;
Dairy cooling room; Staircase, vestibule;
[11 empty] | 7 | Room for keeping and preparing plaster; Rooms for the preparation of paraffin, ozokerite, treatment of pads, washing and drying of sheets, cloths, tarpaulins, regeneration of mud; photo lab; The room of the disinfection rooms; Small animal and waste incineration rooms; Crematories for small animals; Feed room; Rooms for washing and sterilizing dishes, washing and drying films, sanitary room, rooms for enemas, sanitary filters; Passage corridors, vestibules; | 75 | xx | 1,85 | 3,7 | 3,9 | 16,5
[11 empty] | 8 | Sleep treatment room; the control room of the x-ray departments, the x-ray operations unit, the x-ray computed tomography room; Rooms for keeping dead bodies; Rooms for funeral accessories; | 50 | xx | 1,23 | 1,44 | 1728 | 9,26
[11 empty] | 9 | Room for temporary storage of roentgen film; Disinfectant storage room; Rooms and places for keeping portable equipment, stands; Lockers and sheds for storing patient belongings, for clean linen, Sorting rooms and linen storage. | 30 | xx | 0,64 | 0,72 | 0,864 | 4,85
[11 empty] | 10 | Dark rooms for ophthalmologists, soundproof cabin | 20 | xx | 0,58 | 0,576 | 0,864 | 3,09

## Equipment
Electric devices before renovation
No. | Electric device (or devices group) | Power unit [kW] | Units | Total Power kW | Hours of operation [hours] |  | Utilization coeficient |  | Annual consumption [kWh/y]
[5 empty] | During heating season | During cooling season | During heating season | During cooling season
3-DMTT
Electrical technological devices
1 | TV | 0.2 | 13 | 2.6 | 120 | 120 | 0.36 | 0.37 | 227.76 | 115.44
2
3 | Dazmol | 2.5 | 1 | 2.5 | 125 | 125 | 0.48 | 0.47 | 296.875 | 146.875
4 |  |  |  | 0 |  |  |  |  | 0 | 0
5 |  |  |  | 0 |  |  |  |  | 0 | 0
6 |  |  |  | 0 |  |  |  |  | 0 | 0
7 |  |  |  | 0 |  |  |  |  | 0 | 0
8 |  |  |  | 0 |  |  |  |  | 0 | 0
9 |  |  |  | 0 |  |  |  |  | 0 | 0
10 |  |  |  | 0 |  |  |  |  | 0 | 0
11 |  |  |  | 0 |  |  |  |  | 0 | 0
12 |  |  |  | 0 |  |  |  |  | 0 | 0
Technological equipment (kitchen)
1 | Termos | 1.5 | 2 | 3 | 125 | 125 | 0.48 | 0.47 | 356.25 | 176.25
2
3 | Electric stove | 15 | 2 | 30 | 500 | 500 | 0.52 | 0.54 | 15900 | 8100
4 | Meat grinder | 1 | 1 | 1 | 140 | 140 | 0.45 | 0.46 | 127.4 | 64.4
5 | Refrigerators (new) | 0.8 | 3 | 2.4 | 467 | 467 | 0.63 | 0.64 | 1423.416 | 717.312
6 | Refrigerators (old) | 1.2 | 2 | 2.4 | 467 | 467 | 0.63 | 0.64 | 1423.416 | 717.312
7 |  |  |  | 0 |  |  |  |  | 0 | 0
8 |  |  |  | 0 |  |  |  |  | 0 | 0
9 |  |  |  | 0 |  |  |  |  | 0 | 0
10 |  |  |  | 0 |  |  |  |  | 0 | 0
11 |  |  |  | 0 |  |  |  |  | 0 | 0
12 |  |  |  | 0 |  |  |  |  | 0 | 0
13 |  |  |  | 0 |  |  |  |  | 0 | 0
Laundry technological equipment
1 | Washing machine | 2 | 1 | 2 | 417 | 417 | 0.45 | 0.46 | 758.94 | 383.64
Ventilation and air conditioning units
1 |  |  |  | 0 |  |  |  |  | 0
2
Other electrical devices (computers, coffee machines etc)
1 | Computers | 0.2 | 2 | 0.4 | 1440 | 1557 | 0.9 | 0.9 | 1078.92 | 560.52
2 | Printers | 1 | 2 | 2 | 143 | 143 | 0.08 | 0.09 | 48.62 | 25.74
3 | Proektor | 0.2 | 1 | 0.2 | 217 | 217 | 0.11 | 0.12 | 9.982 | 5.208
4 |  |  |  | 0 |  |  |  |  | 0
5 |  |  |  | 0 |  |  |  |  | 0 | 0
6 |  |  |  | 0 |  |  |  |  | 0 | 0
7 |  |  |  | 0 |  |  |  |  | 0 | 0
8 |  |  |  | 0 |  |  |  |  | 0 | 0
Elevators
1 |  |  |  | 0 |  |  |  |  | 0 | 0
2 |  |  |  | 0 |  |  |  |  | 0 | 0
Total annual energy used by equipment before renovation | [8 empty] | 21651.579 | 11012.697
Electric devices after renovation
No. | Electric device (or devices group) | Power [kW] | Units | Total Power kW | Hours of operation [hours] |  | Utilization coeficient |  | Annual consumption [kWh/y]
[5 empty] | During heating season | During cooling season | During heating season | During cooling season
3-DMTT
Electrical technological devices
1 | TV | 0.2 | 13 | 2.6 | 120 | 120 | 0.36 | 0.37 | 227.76 | 115.44
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Dazmol | 2 | 1 | 2 | 125 | 0.48 | 0.47 | 0.47 | 117.9512 | 0.4512
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technological equipment (kitchen)
1 | Termos | 1.5 | 2 | 3 | 125 | 125 | 0.48 | 0.47 | 356.25 | 176.25
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Electric stove | 10 | 2 | 20 | 500 | 500 | 0.52 | 0.54 | 10600 | 5400
4 | Meat grinder | 1 | 1 | 1 | 140 | 140 | 0.45 | 0.46 | 127.4 | 64.4
5 | Refrigerators (new) | 0.8 | 3 | 2.4 | 467 | 467 | 0.63 | 0.64 | 1423.416 | 717.312
6 | Refrigerators (old) | 0.8 | 2 | 1.6 | 467 | 467 | 0.63 | 0.64 | 948.944 | 478.208
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Laundry technological equipment
1 | Washing machine | 2 | 1 | 2 | 417 | 417 | 0.45 | 0.46 | 758.94 | 383.64
Ventilation and air conditioning units
1
2 | AHU's with heat recovery | 0.04 | 41.8 | 1.672 | 1660 | 900 | 0.8 | 0.8 | 3424.256
3
Other electrical devices (computers, coffee machines etc)
1 | Computers | 0.2 | 2 | 0.4 | 1440 | 1557 | 0.9 | 0.9 | 1078.92 | 560.52
2 | Printers | 1 | 2 | 2 | 143 | 143 | 0.08 | 0.09 | 48.62 | 25.74
3 | Proektor | 0.2 | 1 | 0.2 | 217 | 217 | 0.11 | 0.12 | 9.982 | 5.208
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Elevators
1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total annual energy used by equipment after renovation | [8 empty] | 15698.1832 | 7927.1692
[8 empty] | savings | 5953.3958
CAPEX
Replacement of inneficient electrical equipment
No. | Description | Cost [USD/unit] |  |  | Units | Total Investment [USD]
1 | Washing machine | 500 |  |  | 1 | 500
2 | Dazmol | 70 |  |  | 1 | 70
3 | Refrigerater A++ | 300 |  |  | 2 | 600
4 | Induction stove | 1500 |  |  | 2 | 3000
5
6
7
8
9
10
Total for equipment replacement | [5 empty] | 4170

## Cooling
| Space name | Element |  | Orientation | Glazed Area [m²] | Reduction factor g value | Shading reduction factor | Solar radiation |  |  |  |  | Q [kWh/y]
[kWh/m²]
[8 empty] | V* | VI | VII | VIII | IX*
|  | Window |  | S | 79.02 | 0.75 | 0.8 | 31.5 | 65 | 68 | 61 | 31 | 12161.178
|  | Window |  | E | 10.8 | 0.75 | 0.8 | 59 | 125 | 135 | 106 | 39.5 | 3009.96
|  | Window |  | SE | 0 | 0.75 | 0.8 | 52.5 | 111 | 120 | 99 | 41 | 0
|  | Window |  | SW | 0 | 0.75 | 0.8 | 52.5 | 111 | 120 | 99 | 41 | 0
|  | Window |  | NE | 0 | 0.75 | 0.8 | 45 | 93 | 98 | 76 | 24.5 | 0
|  | Window |  | NW | 0 | 0.75 | 0.8 | 45 | 93 | 98 | 76 | 24.5 | 0
Window
Window
| Total annual solar heat gains before renovation | [11 empty] | 15171.138
| 0 | Window |  | S | 79.02 | 0.5 | 0.8 | 31.5 | 65 | 68 | 61 | 31 | 8107.452
| 0 | Window |  | E | 10.8 | 0.5 | 0.8 | 59 | 125 | 135 | 106 | 39.5 | 3009.96
| 0 | Window |  | SE | 0 | 0.5 | 0.8 | 52.5 | 111 | 120 | 99 | 41 | 0
| 0 | Window |  | SW | 0 | 0.5 | 0.8 | 52.5 | 111 | 120 | 99 | 41 | 0
| 0 | Window |  | NE | 0 | 0.5 | 0.8 | 45 | 93 | 98 | 76 | 24.5 | 0
| 0 | Window |  | NW | 0 | 0.5 | 0.8 | 45 | 93 | 98 | 76 | 24.5 | 0
| 0 | Window | [10 empty] | #VALUE!
| 0 | Window | [10 empty] | #VALUE!
| Total annual solar heat gains after renovation | [11 empty] | #VALUE!
Total solar heat gains savings from replacement of openings | [12 empty] | #VALUE!
[19 empty] | V* | VI. | VII. | VIII. | IX*
[18 empty] | S | 31.5 | 65 | 68 | 61 | 31
[18 empty] | N | 26.5 | 54 | 53 | 44 | 17
[18 empty] | E | 59 | 125 | 135 | 106 | 39.5
[18 empty] | W | 59 | 125 | 135 | 106 | 39.5
[18 empty] | SE | 52.5 | 111 | 120 | 99 | 41
[18 empty] | SW | 52.5 | 111 | 120 | 99 | 41
[18 empty] | NE | 45 | 93 | 98 | 76 | 24.5
Equipment heat gains before renovation | [7 empty] | Equipment heat gains after renovation | [6 empty] | glazing type | Factor transmission of total solar energy when falling on the perpendicular surface, |  | NW | 45 | 93 | 98 | 76 | 24.5
No. | Block/floor name | Annual heat gains from equipment [kWh/y] | Solar heat gains [kWh/y] | Total needs for cooling [kWh/y] | Seasonal Coefficient of Performance (SEER) | Electrical energy used for cooling purposes [kWh/y] |  | No. | Block/floor name | Annual heat gains from equipment [kWh/y] | Solar heat gains [kWh/y] | Total needs for cooling [kWh/y] | Seasonal Coefficient of Performance (SEER) | Electrical energy used for cooling purposes [kWh/y] |  | gn |  | Horizontal | 119.7 | 244.7 | 243.6 | 204.4 | 81.8
1 | [7 empty] | 1 | [6 empty] | Average glazing | 0,85 |  | * Only 15 days out of 30 are applied in calculations
2 | 3-DMTT | 11012.697 | 15171.138 | 26183.835 | 3.2 | 8182.4484 |  | 2 | 3-DMTT | 7927.1692 | #VALUE! | #VALUE! | 8.5 | #VALUE! | double glazing | 0,75
3 | [7 empty] | 3 | 0 | [5 empty] | Double glazing coated with selective low-e | 0,67
4 |  |  |  | 0 | 3.2 | 0 |  | 4 |  |  | 0 | 0 | 8.5 | 0 | triple glazing | 0,70
5 |  |  |  | 0 | 3.2 | 0 |  | 5 |  |  | 0 | 0 | 8.5 | 0 | Triple glazing with double selective low-e coating | 0,50
Total |  |  |  | 26183.835 |  | 8182.4484 |  | Total |  |  |  | #VALUE! |  | #VALUE! | double window | 0,75
[12 empty] | savings | #VALUE!
CAPEX
Actually installed air conditioners | [14 empty] | Installation of centralized air cooling system
[15 empty] | Description | Units
No. | Installed air conditioner systems | Power [kW] | No of units | Installed power [kW] | Hours of operation during cooling season [hours] |  | Q cooling [kWh/y] | [7 empty] | Compressor-Condensing Unit capacity [kW] | 0 | #DIV/0!
[15 empty] | Compressor-Condensing Units equipped with heat pump function with Seasonal Energy Efficiency Ratio (SEER) of at least 8.5 [USD/kW] | 340
[15 empty] | Investment cost for fully functional freon based system which includes compressor-condensate units with heat pump function and distribution system connected to AHU units | 0
3 | Split systems | 1.5 | 14 | 21 | 0 |  | 0 | [7 empty] | Labour | 0
Total electrical energy consumption used for cooling before renovation | [6 empty] | 0 | [7 empty] | Total | 0

## PV
PV system potential |  |  |  | https://re.jrc.ec.europa.eu/pvg_tools/en/
Description | Area [m²]
Availability of roof space for PV installation | 558.182
Necessary area for 1kW PV installation under 45° angle | 10
Capacity of PV system planned to be installed | 10 | should not exceed the installed electrical capacity
Availability of roof space after PV system installation | 458.182
Electricity production from the proposed system
Month | Monthly electricity production [kWh]
January | 1023.37
February | 1042.11
March | 1307.37
April | 1414.05
May | 1470.9
June | 1464.09
July | 1583.16
August | 1622.82
September | 1534.55
October | 1266.93
November | 967.54
December | 910.53
Total annual production [kWh/y] | 15607.42
Installation of PV system
Description | Unit cost [USD/kW] | Foreseen capacity [kW] | Total [USD]
Monocrystaline PV panels including on-grid inverter, materials and labour | 726.8 | 10 | 7268

## Solar DHW
DHW solar system potential
Description | Area [m²]
Availability of roof space for solar DHW installation | 500
Necessary area for one solar DHW panel of 2.5m² under 45° angle | 4
Number of solar DHW collectors planned to be installed | 4 | Reduce number of Collectors!!!
Availability of roof space after solar DHW system installation | 484
Thermal energy produced from solar DHW
| No of units | Area of one solar collector [m²] | Average generation during warm period [kWh/m²] | Average generation during cold period [kWh/m²] | Hours of generation during warm period [h] | Hours of generation during cold period [h] | DHW generation Q [kWh/y] |  | S | litres | MD average daily warm kWh/m2y | MD average daily cold kWh/m2y | kWh/m2 warm | kWh/m2 cold
Tube type solar collector of 2.5m² | 0 | 2.5 | 0.78 | 0.64 | 1095 | 730 | 0 | Vitosol 200-t | 2.5 | 25 | 1.95 | 1.6 | 0.78 | 0.64
Proposed solar DHW capacity | 4 | 2.5 | 0.78 | 0.64 | 1095 | 730 | 7927.8
Installation of solar DHW system
Equipment | No of units | Price per unit [USD] | Total [USD]
Boiler of 1000l, with 2 integrated heat exchangers (1 for solar collectors and 1 for district heating) | 1 | 6900 | 6900
Tube type solar collector with area of 2,5m² | 4 | 1800 | 7200
Automatization | 1 | 1800 | 1800
Water treatment | 1 | 3000 | 3000
Pumps | 2 | 1600 | 3200
Expansions tanks, valves, fitings, pipes & insullation | 4 | 715 | 2860
Total investment per DHW equipment |  |  | 24960
Labour |  |  | 7488
Total cost for a complete and functional system |  |  | 4000 |  | Installed at Block 2

## Shading
| Space name | Element | Type | Orientation | Glazed Area [m²] | Reduction factor g value | Shading reduction factor | Solar radiation |  |  |  |  | Q [kWh/y]
[kWh/m²]
[8 empty] | V* | VI | VII | VIII | IX*
After renovation |  | Window | 0 | S | 79.02 | 0.5 | 0.8 | 31.5 | 65 | 68 | 61 | 31 | 8107.452
|  | Window | 0 | E | 10.8 | 0.5 | 0.8 | 59 | 125 | 135 | 106 | 39.5 | 2006.64
|  | Window | 0 | NW | 0 | 0.5 | 0.8 | 45 | 93 | 98 | 76 | 24.5 | 0
|  | Window | 0 | 0 | 0 | 0 | 0 | [7 empty] | Input data table with shading factors:
|  | Window | 0 | 0 | 0 | 0 | 0 | [7 empty] | Type of shading element |  | Factor
| Total annual solar heat gains after renovation | [11 empty] | 10114.092 | No of openings | Fixed horizontal shading (S, SW and SE) |  | 0.7
After renovation |  | Window | 0 | S | 79.02 | 0.5 | 0.8 | 31.5 | 65 | 68 | 61 | 31 | 8107.452 | 0
|  | Window | 0 | E | 10.8 | 0.5 | 0.8 | 59 | 125 | 135 | 106 | 39.5 | 2006.64 | 0
|  | Window | 0 | NW | 0 | 0.5 | 0.8 | 45 | 93 | 98 | 76 | 24.5 | 0 | 0
|  | Window | 0 | 0 | 0 | 0 | 0.8 | [6 empty] | 0
|  | Window | 0 | 0 | 0 | 0 | 0.8 | [6 empty] | 0
| Total annual solar heat gains after renovation with installed shading elements | [11 empty] | 10114.092
Total solar heat gains savings from shading elements installation | [12 empty] | 0
[19 empty] | V* | VI. | VII. | VIII. | IX*
[18 empty] | S | 31.5 | 65 | 68 | 61 | 31
Description |  |  |  |  | Unit | [12 empty] | N | 26.5 | 54 | 53 | 44 | 17
Electrical energy used for cooling purposes before renovation [kWh/y] |  |  |  |  | 8182.4484 | [12 empty] | E | 59 | 125 | 135 | 106 | 39.5
Annual solar heat gains savings from installed shading elements [kWh/y] |  |  |  |  | 0 | [12 empty] | W | 59 | 125 | 135 | 106 | 39.5
Seasonal Energy Efficiency Ratio (SEER) after renovation |  |  |  |  | 8.5 | [12 empty] | SE | 52.5 | 111 | 120 | 99 | 41
Annual electrical energy savings from installed shading elements [kWh/y] |  |  |  |  | 0 | [12 empty] | SW | 52.5 | 111 | 120 | 99 | 41
Electrical energy used for cooling purposes after renovation [kWh/y] |  |  |  |  | 8182.4484 | [12 empty] | NE | 45 | 93 | 98 | 76 | 24.5
[15 empty] | glazing type | Factor transmission of total solar energy when falling on the perpendicular surface, |  | NW | 45 | 93 | 98 | 76 | 24.5
| CAPEX | [14 empty] | gn |  | Horizontal | 119.7 | 244.7 | 243.6 | 204.4 | 81.8
| Installation of shading elements at the windows | [13 empty] | Average glazing | 0,85 |  | * Only 15 days out of 30 are applied in calculations | [5 empty] | Pictures from GIZ MLPS Project (Leova, Moldova)
| Description | Units | [12 empty] | double glazing | 0,75
| Instalaltion of exterior fixed horizontal shading elements at the windows performed from: at least 1mm thick stainless steel applied powder paint layer in spray chamber, polymerization of powder coating in a polymerization stove. [USD/unit] | 140 | [12 empty] | Double glazing coated with selective low-e | 0,67
| Number of shading elements to be installed |  | A se întroduce numărul total (nu suprafața) de ferestre orientate spre Sud, Sud-Est, Sud-Vest, Vest si Est la care a fost aplicat factorul de umbrire | [11 empty] | triple glazing | 0,70
| Total | 0 | [12 empty] | Triple glazing with double selective low-e coating | 0,50
| Labour | 0 | [12 empty] | double window | 0,75
| Total including labour | 0

## EMS
Implementation of EMS system
Energy needs | Based on standardized conditions [kWh/y] | Annual energy savings after implementation of EMS system [kWh/y]
Heating | 149011.4805 | 4470.3444
DHW | 0 | 0
Cooling | 0 | 0
Lighting | 16687.5147 | 500.6254
Total annual thermal energy savings [kWh/y] |  | 4470.3444
Total annual electrical energy savings [kWh/y] |  | 500.6254
CAPEX
Description | Cost [USD]
Installation of Energy Management System. Foresees installation of smart meters at dilimitation points for thermal and electrical energy. Additional meters, controllers & valves for remote control and reading installed for heating, DHW, Cooling & Lighting.

## Overall gener. & distrib. eff.
| Description of source | Before renovation (standardized) | [5 empty] | After renovation (standardized)
|  | Useful energy needs [kWh/y] | Needs covered [%] | Distribution energy losses [kWh/y] | Generation efficiency** | Final energy consumption [kWh/y] | Specific final energy consumption [kWh/m²·y] | Useful energy needs [kWh/y] | Needs covered [%] | Distribution energy losses [kWh/y] | Generation efficiency** | Final energy consumption [kWh/y] | Specific final energy consumption [kWh/m²·y]
Heating |  |  | 0% |  | 100% | 0 |  |  | 0% |  |  | 0
|  |  | 0% |  | 100% | 0 |  |  | 0% |  |  | 0
| Gas boiler | 401152.9367 | 100% | 36772.8 | 58% | 621854.5462 |  | 136064.9403 | 100% | 8606.4 | 97% | 149011.4805
| Total | 401152.9367 | 100% |  |  | 562812.7253 | 223.7455 | 136064.9403 | 100% |  |  | 85499.3153 | 33.9901
DHW |  | 0 | 0% | 0 | 98% | 0 |  |  | 0% |  | 98% | 0
| Electrical boilers | 4094.6032 | 100% | 683.7987 | 100% | 4778.4019 |  |  | 0% | 0 | 100% | 0
| Solar DHW |  | 0% |  |  | 0 |  | -7927.8 | -100% |  | 100% | -7927.8
| Total | 4094.6032 | 100% |  |  | 4778.4019 | 1.8996 | -7927.8 | -100% |  |  | -7927.8 | -3.1517
Cooling |  | 0 | 0% | 0 | 3.2 | 0 |  |  | #DIV/0! | 0 | 8.5 | 0
|  |  | 0% |  |  | 0 |  |  | #DIV/0! |  |  | 0
|  |  | 0% |  |  | 0 |  |  | #DIV/0! |  |  | 0
| Total | 26183.835 | 0% |  |  | 0 | #DIV/0! | 0 | #DIV/0! |  |  | 0 | #DIV/0!
[6 empty] | 567591.1272 |  |  | 490019.612 |  |  | 77571.5153

## Breakdown Baseline & Balance
Type of energy | Needs | Before renovation |  |  | After renovation
|  | Theoretical energy needs based on standardized conditions [kWh/y] | ratio | Actual energy consumption (Baseline) [kWh/y] | Energy needs based on standardized conditions [kWh/y] | Theoretical energy savings based on standardized conditions [kWh/y] | Actual energy savings based on standardized conditions [kWh/y]
Thermal energy | Walls | 95776.5591 | 17.02% | 40904.2145 | 20512.7097 | 75263.8494 | 20391.5048
| Roof | 123019.0423 | 21.86% | 52538.9233 | 18573.7215 | 104445.3208 | 33965.2018
| Floor | 14809.5053 | 2.631% | 6324.8376 | 14809.5053 | 0 | -8484.6677
| Windows and Doors | 26215.3788 | 4.658% | 11196.0535 | 13398.9237 | 12816.4551 | -2202.8702
| Ventilation | 141332.4513 | 25.11% | 60360.2067 | 68770.0802 | 72562.3711 | -8409.8735
| DHW needs and distribution | 0 | 0% | 0 | 4094.6032 | -4094.6032 | -4094.6032
| Heat Distribution | 36772.8 | 6.534% | 15704.9127 | 8606.4 | 28166.4 | 7098.5127
| Generation Heating +DHW | 183928.8094 | 32.68% | 78552.2423 | 4081.9482 | 179846.8612 | 74470.2941
| Gains heating season | -59041.8209 | -10.49% |  | -59041.8209
| Solar DHW |  |  |  | -7927.8 | 7927.8 | 7927.8
| EMS |  |  |  | -4470.3444 | 4470.3444 | 4470.3444
Total | Total | 562812.7253 | 100% | 240365.8333 | 81407.9264 | 481404.7989 | 125131.6432
Electrical energy | Lighting | 40068.0757 | 60.25% | 33769.6381 | 16186.8892 | 23881.1865 | 17582.7488
| Equipment | 21651.579 | 32.56% | 18248.0934 | 15698.1832 | 5953.3958 | 2549.9102
Cooling
| DHW | 4778.4019 | 7.186% | 4778.4019 | 0 | 4778.4019 | 4778.4019
| Heating | 0 | 0% | 0 | 0 | 0 | 0
| Ventilation | 0 | 0% | 0 | 3424.256 | -3424.256 | -3424.256
| PV |  |  |  | -15607.42 | 15607.42 | 15607.42
Gains cooling season
| EMS |  |  |  | -500.6254 | 500.6254 | 500.6254
Total | Total | 66498.0566 | 100% | 56045 | 19201.283 | 47296.7737 | 37594.8503
|  | Actual according to the bills | Standardized before renovation | Standardized after renovation
| Specific final thermal energy consumption for heating [kWh/m²·y] | 95.5571 | 223.7455 | 33.9901
| Specific final thermal energy consumption for DHW [kWh/m²·y] | 0 | 1.8996 | -3.1517
| Specific final electrical energy consumption [kWh/m²·y] | 22.2806 | 26.4362 | 7.6334
Thermal
[9 empty] | DATA | Invisible | difference | Percentage | Text
[8 empty] | Actual energy consumption according to the bills before renovation | 240365.8333
[8 empty] | Energy needs based on standardized conditions before renovation | 562812.7253 | 240365.8333 | 158957.9069 | 66.13%
[8 empty] | Energy needs based on standardized conditions after renovation | 81407.9264
Electrical
[9 empty] | DATA | Invisible | difference | Percentage | Text
[8 empty] | Actual energy consumption according to the bills before renovation | 56045
[8 empty] | Energy needs based on standardized conditions before renovation | 66498.0566 | 56045 | 36843.717 | 65.74%
[8 empty] | Energy needs based on standardized conditions after renovation | 19201.283

## Non-EE measures
No | Non-EE Measures | Description | Unit of measure | No of units | Unit cost [USD] | Total cost [USD]
1 | Elektr kabellarini va tarqatish shkaflarini almashtirish | Eski kabel izolyatsiyasi yaroqsiz, qisqa tutashuv xavfi. Yoritish va asbob-uskunalarni yangilashda majburiy. | units | 20 | 200 | 4000
2 | Ichki devorlarni gipslash va bo‘yash (fasad ichki qismi) | Izolyatsiya va deraza o‘rnatishdan keyin devorlar shikastlanadi, ularni tekislash va bo‘yash kerak. | m2 | 500 | 10 | 5000
3 | Eski isitish quvurlarini (podvalda) demontaj qilish | Agar tizim butunlay almashtirilayotgan bo‘lsa, eski quvurlarni olib tashlash kerak. | m | 50 | 40 | 2000
4
5
6
7
8
9
10
11
12
13

## Financial indicators
Measure: | Thermal insulation of walls
№ | Indicators | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2026: 76137.9
1.2 | Maintenance costs (CM), [USD] |  | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895 | 380.6895
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | 1647.2286 | 1779.0068 | 1910.7851 | 2042.5634 | 2174.3417 | 2306.12 | 2437.8983 | 2569.6765 | 2701.4548 | 2833.2331 | 2965.0114 | 3096.7897 | 3228.568 | 3360.3463 | 3492.1245 | 3623.9028 | 3755.6811 | 3887.4594 | 4019.2377 | 4151.016
2.2 | Gross actual savings, [USD] | 0 | 446.2895 | 481.9927 | 517.6959 | 553.399 | 589.1022 | 624.8054 | 660.5085 | 696.2117 | 731.9149 | 767.618 | 803.3212 | 839.0243 | 874.7275 | 910.4307 | 946.1338 | 981.837 | 1017.5402 | 1053.2433 | 1088.9465 | 1124.6496
2.3 | Net standard savings, [USD] | -76137.9 | 1266.5391 | 1398.3173 | 1530.0956 | 1661.8739 | 1793.6522 | 1925.4305 | 2057.2088 | 2188.987 | 2320.7653 | 2452.5436 | 2584.3219 | 2716.1002 | 2847.8785 | 2979.6568 | 3111.435 | 3243.2133 | 3374.9916 | 3506.7699 | 3638.5482 | 3770.3265
2.4 | Net actual savings, [USD] | -76137.9 | 65.6 | 101.3032 | 137.0064 | 172.7095 | 208.4127 | 244.1159 | 279.819 | 315.5222 | 351.2254 | 386.9285 | 422.6317 | 458.3348 | 494.038 | 529.7412 | 565.4443 | 601.1475 | 636.8507 | 672.5538 | 708.257 | 743.9601
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | -76137.9 | 1583.8736 | 1644.7918 | 1698.681 | 1745.9918 | 1787.1504 | 1822.5601 | 1852.6023 | 1877.6375 | 1898.0063 | 1914.0308 | 1926.0149 | 1934.2457 | 1938.9943 | 1940.5162 | 1939.0528 | 1934.8313 | 1928.0662 | 1918.9593 | 1907.7007 | 1894.4695
3.2 | Actualized actual net savings, [USD] | -76137.9 | 429.1246 | 445.6294 | 460.2297 | 473.0478 | 484.1991 | 493.7928 | 501.9322 | 508.7151 | 514.2337 | 518.5752 | 521.8221 | 524.0521 | 525.3387 | 525.751 | 525.3545 | 524.2108 | 522.3779 | 519.9105 | 516.8602 | 513.2754
3.3 | Standardized NPV¹, [USD] | 2026: -44223.418
3.4 | Actual NPV², [USD] | 2026: -71263.1618
3.5 | Accumulated net discounted standardized savings, [USD] | -76137.9 | -74554.0264 | -72909.2346 | -71210.5535 | -69464.5618 | -67677.4114 | -65854.8513 | -64002.249 | -62124.6115 | -60226.6052 | -58312.5744 | -56386.5595 | -54452.3138 | -52513.3196 | -50572.8033 | -48633.7505 | -46698.9192 | -44770.853 | -42851.8937 | -40944.193 | -39049.7235
3.6 | Accumulated net discounted actual savings, [USD] | -76137.9 | -75708.7754 | -75263.1461 | -74802.9163 | -74329.8685 | -73845.6695 | -73351.8767 | -72849.9445 | -72341.2295 | -71826.9958 | -71308.4206 | -70786.5984 | -70262.5463 | -69737.2076 | -69211.4566 | -68686.1021 | -68161.8913 | -67639.5134 | -67119.6029 | -66602.7427 | -66089.4673
3.7 | Discounted payback period based on standardized conditions [years] | 2026: #N/A
3.8 | Discounted actual payback period [years] | 2026: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2026: -3.196%
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2026: -13.88%
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | Replacement of windows and doors
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: 16623.75
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | 280.5016 | 264.7935 | 272.6476 | 280.5016 | 288.3557 | 296.2097 | 304.0637 | 311.9178 | 319.7718 | 327.6259 | 335.4799 | 343.334 | 351.188 | 359.0421 | 366.8961 | 374.7501 | 382.6042 | 390.4582 | 398.3123 | 406.1663
2.2 | Gross actual savings, [USD] | 0 | -48.2121 | -45.5123 | -46.8622 | -48.2121 | -49.5621 | -50.912 | -52.262 | -53.6119 | -54.9618 | -56.3118 | -57.6617 | -59.0117 | -60.3616 | -61.7115 | -63.0615 | -64.4114 | -65.7613 | -67.1113 | -68.4612 | -69.8112
2.3 | Net standard savings, [USD] | -16623.75 | -2765.0144 | -2780.7225 | -2772.8684 | -2765.0144 | -2757.1603 | -2749.3063 | -2741.4523 | -2733.5982 | -2725.7442 | -2717.8901 | -2710.0361 | -2702.182 | -2694.328 | -2686.4739 | -2678.6199 | -2670.7659 | -2662.9118 | -2655.0578 | -2647.2037 | -2639.3497
2.4 | Net actual savings, [USD] | -16623.75 | -3093.7281 | -3091.0283 | -3092.3782 | -3093.7281 | -3095.0781 | -3096.428 | -3097.778 | -3099.1279 | -3100.4778 | -3101.8278 | -3103.1777 | -3104.5277 | -3105.8776 | -3107.2275 | -3108.5775 | -3109.9274 | -3111.2773 | -3112.6273 | -3113.9772 | -3115.3272
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | -16623.75 | 269.7131 | 244.8165 | 242.3827 | 239.774 | 237.0073 | 234.0988 | 231.0635 | 227.9153 | 224.6674 | 221.3323 | 217.9214 | 214.4454 | 210.9144 | 207.3378 | 203.7244 | 200.0822 | 196.4188 | 192.7412 | 189.0559 | 185.369
3.2 | Actualized actual net savings, [USD] | -16623.75 | -46.3578 | -42.0786 | -41.6603 | -41.2119 | -40.7364 | -40.2365 | -39.7148 | -39.1737 | -38.6155 | -38.0422 | -37.4559 | -36.8585 | -36.2516 | -35.6369 | -35.0158 | -34.3898 | -33.7601 | -33.128 | -32.4946 | -31.8609
3.3 | Standardized NPV¹, [USD] | 2023: -53622.5251
3.4 | Actual NPV², [USD] | 2023: -58767.9862
3.5 | Accumulated net discounted standardized savings, [USD] | -16623.75 | -16354.0369 | -16109.2204 | -15866.8377 | -15627.0638 | -15390.0565 | -15155.9576 | -14924.8942 | -14696.9789 | -14472.3114 | -14250.9791 | -14033.0578 | -13818.6124 | -13607.698 | -13400.3601 | -13196.6357 | -12996.5536 | -12800.1348 | -12607.3937 | -12418.3377 | -12232.9687
3.6 | Accumulated net discounted actual savings, [USD] | -16623.75 | -16670.1078 | -16712.1865 | -16753.8468 | -16795.0587 | -16835.7951 | -16876.0316 | -16915.7464 | -16954.9201 | -16993.5355 | -17031.5778 | -17069.0337 | -17105.8922 | -17142.1438 | -17177.7807 | -17212.7965 | -17247.1863 | -17280.9464 | -17314.0744 | -17346.569 | -17378.4299
3.7 | Discounted payback period based on standardized conditions [years] | 2023: #N/A
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: #NUM!
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: #NUM!
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | Thermal insulation of the roof
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: 15350.1
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | 2285.8958 | 2157.8856 | 2221.8907 | 2285.8958 | 2349.9009 | 2413.9059 | 2477.911 | 2541.9161 | 2605.9212 | 2669.9263 | 2733.9313 | 2797.9364 | 2861.9415 | 2925.9466 | 2989.9517 | 3053.9567 | 3117.9618 | 3181.9669 | 3245.972 | 3309.9771
2.2 | Gross actual savings, [USD] | 0 | 743.3642 | 701.7358 | 722.55 | 743.3642 | 764.1784 | 784.9926 | 805.8068 | 826.621 | 847.4352 | 868.2494 | 889.0636 | 909.8778 | 930.692 | 951.5062 | 972.3204 | 993.1346 | 1013.9488 | 1034.763 | 1055.5771 | 1076.3913
2.3 | Net standard savings, [USD] | -15350.1 | -759.6202 | -887.6304 | -823.6253 | -759.6202 | -695.6151 | -631.6101 | -567.605 | -503.5999 | -439.5948 | -375.5897 | -311.5847 | -247.5796 | -183.5745 | -119.5694 | -55.5643 | 8.4407 | 72.4458 | 136.4509 | 200.456 | 264.4611
2.4 | Net actual savings, [USD] | -15350.1 | -2302.1518 | -2343.7802 | -2322.966 | -2302.1518 | -2281.3376 | -2260.5234 | -2239.7092 | -2218.895 | -2198.0808 | -2177.2666 | -2156.4524 | -2135.6382 | -2114.824 | -2094.0098 | -2073.1956 | -2052.3814 | -2031.5672 | -2010.753 | -1989.9389 | -1969.1247
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | -15350.1 | 2197.9767 | 1995.0865 | 1975.2527 | 1953.9933 | 1931.4472 | 1907.7449 | 1883.0087 | 1857.3532 | 1830.8857 | 1803.7065 | 1775.9097 | 1747.5828 | 1718.8079 | 1689.6612 | 1660.214 | 1630.5325 | 1600.6782 | 1570.7083 | 1540.676 | 1510.6303
3.2 | Actualized actual net savings, [USD] | -15350.1 | 714.7733 | 648.7942 | 642.3443 | 635.4308 | 628.0989 | 620.391 | 612.3469 | 604.0039 | 595.3967 | 586.5582 | 577.5187 | 568.307 | 558.9495 | 549.4711 | 539.895 | 530.2427 | 520.5342 | 510.7881 | 501.0217 | 491.251
3.3 | Standardized NPV¹, [USD] | 2023: -20957.7998
3.4 | Actual NPV², [USD] | 2023: -45103.5393
3.5 | Accumulated net discounted standardized savings, [USD] | -15350.1 | -13152.1233 | -11157.0368 | -9181.784 | -7227.7907 | -5296.3435 | -3388.5986 | -1505.5899 | 351.7633 | 2182.649 | 3986.3555 | 5762.2651 | 7509.848 | 9228.6559 | 10918.3171 | 12578.5312 | 14209.0636 | 15809.7418 | 17380.4502 | 18921.1262 | 20431.7565
3.6 | Accumulated net discounted actual savings, [USD] | -15350.1 | -14635.3267 | -13986.5326 | -13344.1882 | -12708.7574 | -12080.6585 | -11460.2674 | -10847.9205 | -10243.9167 | -9648.52 | -9061.9618 | -8484.443 | -7916.1361 | -7357.1866 | -6807.7155 | -6267.8205 | -5737.5779 | -5217.0437 | -4706.2556 | -4205.2339 | -3713.983
3.7 | Discounted payback period based on standardized conditions [years] | 2023: 8.8106
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: #NUM!
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: #NUM!
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | #REF!
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: #REF!
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2.2 | Gross actual savings, [USD] | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2.3 | Net standard savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2.4 | Net actual savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.2 | Actualized actual net savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.3 | Standardized NPV¹, [USD] | 2023: #REF!
3.4 | Actual NPV², [USD] | 2023: #REF!
3.5 | Accumulated net discounted standardized savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.6 | Accumulated net discounted actual savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.7 | Discounted payback period based on standardized conditions [years] | 2023: #N/A
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: #VALUE!
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: #VALUE!
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | Mechanical ventilation with heat recovery
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: 20139
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | 1274.8403 | 1203.4492 | 1239.1447 | 1274.8403 | 1310.5358 | 1346.2313 | 1381.9268 | 1417.6224 | 1453.3179 | 1489.0134 | 1524.7089 | 1560.4045 | 1596.1 | 1631.7955 | 1667.4911 | 1703.1866 | 1738.8821 | 1774.5776 | 1810.2732 | 1845.9687
2.2 | Gross actual savings, [USD] | 0 | -497.3225 | -469.4725 | -483.3975 | -497.3225 | -511.2476 | -525.1726 | -539.0976 | -553.0227 | -566.9477 | -580.8727 | -594.7978 | -608.7228 | -622.6478 | -636.5728 | -650.4979 | -664.4229 | -678.3479 | -692.273 | -706.198 | -720.123
2.3 | Net standard savings, [USD] | -20139 | -1770.6757 | -1842.0668 | -1806.3713 | -1770.6757 | -1734.9802 | -1699.2847 | -1663.5892 | -1627.8936 | -1592.1981 | -1556.5026 | -1520.8071 | -1485.1115 | -1449.416 | -1413.7205 | -1378.0249 | -1342.3294 | -1306.6339 | -1270.9384 | -1235.2428 | -1199.5473
2.4 | Net actual savings, [USD] | -20139 | -3542.8385 | -3514.9885 | -3528.9135 | -3542.8385 | -3556.7636 | -3570.6886 | -3584.6136 | -3598.5387 | -3612.4637 | -3626.3887 | -3640.3138 | -3654.2388 | -3668.1638 | -3682.0888 | -3696.0139 | -3709.9389 | -3723.8639 | -3737.789 | -3751.714 | -3765.639
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | -20139 | 1225.8079 | 1112.6564 | 1101.5952 | 1089.7388 | 1077.1649 | 1063.9462 | 1050.1508 | 1035.8428 | 1021.0819 | 1005.9241 | 990.4219 | 974.624 | 958.5763 | 942.3213 | 925.8986 | 909.3452 | 892.6956 | 875.9814 | 859.2324 | 842.476
3.2 | Actualized actual net savings, [USD] | -20139 | -478.1947 | -434.0537 | -429.7386 | -425.1134 | -420.2082 | -415.0515 | -409.6699 | -404.0882 | -398.3299 | -392.4168 | -386.3693 | -380.2065 | -373.9461 | -367.605 | -361.1984 | -354.7408 | -348.2457 | -341.7254 | -335.1915 | -328.6548
3.3 | Standardized NPV¹, [USD] | 2023: -41573.0747
3.4 | Actual NPV², [USD] | 2023: -69313.3048
3.5 | Accumulated net discounted standardized savings, [USD] | -20139 | -18913.1921 | -17800.5356 | -16698.9405 | -15609.2017 | -14532.0368 | -13468.0906 | -12417.9398 | -11382.0971 | -10361.0152 | -9355.0911 | -8364.6692 | -7390.0452 | -6431.4689 | -5489.1476 | -4563.249 | -3653.9038 | -2761.2082 | -1885.2268 | -1025.9944 | -183.5184
3.6 | Accumulated net discounted actual savings, [USD] | -20139 | -20617.1947 | -21051.2484 | -21480.9871 | -21906.1005 | -22326.3087 | -22741.3602 | -23151.0301 | -23555.1184 | -23953.4483 | -24345.8651 | -24732.2344 | -25112.4408 | -25486.387 | -25853.9919 | -26215.1903 | -26569.9311 | -26918.1768 | -27259.9022 | -27595.0938 | -27923.7485
3.7 | Discounted payback period based on standardized conditions [years] | 2023: #N/A
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: #NUM!
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: #NUM!
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | Heating system replacement
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: 18000
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | 616.4513 | 581.93 | 599.1907 | 616.4513 | 633.7119 | 650.9726 | 668.2332 | 685.4939 | 702.7545 | 720.0151 | 737.2758 | 754.5364 | 771.797 | 789.0577 | 806.3183 | 823.5789 | 840.8396 | 858.1002 | 875.3609 | 892.6215
2.2 | Gross actual savings, [USD] | 0 | 155.3584 | 146.6583 | 151.0084 | 155.3584 | 159.7085 | 164.0585 | 168.4085 | 172.7586 | 177.1086 | 181.4586 | 185.8087 | 190.1587 | 194.5087 | 198.8588 | 203.2088 | 207.5589 | 211.9089 | 216.2589 | 220.609 | 224.959
2.3 | Net standard savings, [USD] | -18000 | -2429.0647 | -2463.586 | -2446.3253 | -2429.0647 | -2411.8041 | -2394.5434 | -2377.2828 | -2360.0221 | -2342.7615 | -2325.5009 | -2308.2402 | -2290.9796 | -2273.719 | -2256.4583 | -2239.1977 | -2221.9371 | -2204.6764 | -2187.4158 | -2170.1551 | -2152.8945
2.4 | Net actual savings, [USD] | -18000 | -2890.1576 | -2898.8577 | -2894.5076 | -2890.1576 | -2885.8075 | -2881.4575 | -2877.1075 | -2872.7574 | -2868.4074 | -2864.0574 | -2859.7073 | -2855.3573 | -2851.0073 | -2846.6572 | -2842.3072 | -2837.9571 | -2833.6071 | -2829.2571 | -2824.907 | -2820.557
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | -18000 | 592.7416 | 538.027 | 532.6783 | 526.9452 | 520.865 | 514.4731 | 507.8023 | 500.8836 | 493.746 | 486.4164 | 478.9203 | 471.2812 | 463.5213 | 455.6611 | 447.7199 | 439.7155 | 431.6645 | 423.5824 | 415.4834 | 407.3808
3.2 | Actualized actual net savings, [USD] | -18000 | 149.3831 | 135.5939 | 134.2459 | 132.801 | 131.2687 | 129.6578 | 127.9766 | 126.233 | 124.4342 | 122.587 | 120.6978 | 118.7726 | 116.8169 | 114.836 | 112.8346 | 110.8174 | 108.7884 | 106.7515 | 104.7104 | 102.6683
3.3 | Standardized NPV¹, [USD] | 2023: -49740.0471
3.4 | Actual NPV², [USD] | 2023: -56957.6813
3.5 | Accumulated net discounted standardized savings, [USD] | -18000 | -17407.2584 | -16869.2313 | -16336.553 | -15809.6078 | -15288.7428 | -14774.2697 | -14266.4674 | -13765.5838 | -13271.8378 | -12785.4214 | -12306.5011 | -11835.2199 | -11371.6986 | -10916.0374 | -10468.3175 | -10028.602 | -9596.9374 | -9173.355 | -8757.8716 | -8350.4908
3.6 | Accumulated net discounted actual savings, [USD] | -18000 | -17850.6169 | -17715.023 | -17580.7771 | -17447.9761 | -17316.7074 | -17187.0496 | -17059.0729 | -16932.8399 | -16808.4058 | -16685.8188 | -16565.1211 | -16446.3485 | -16329.5316 | -16214.6956 | -16101.8609 | -15991.0436 | -15882.2552 | -15775.5037 | -15670.7934 | -15568.125
3.7 | Discounted payback period based on standardized conditions [years] | 2023: #N/A
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: #NUM!
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: #NUM!
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | #REF!
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: #REF!
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2.2 | Gross actual savings, [USD] | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2.3 | Net standard savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2.4 | Net actual savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.2 | Actualized actual net savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.3 | Standardized NPV¹, [USD] | 2023: #REF!
3.4 | Actual NPV², [USD] | 2023: #REF!
3.5 | Accumulated net discounted standardized savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.6 | Accumulated net discounted actual savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.7 | Discounted payback period based on standardized conditions [years] | 2023: #N/A
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: #VALUE!
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: #VALUE!
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | Replacement of gas boiler
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: 22770
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | 3936.1378 | 3715.7141 | 3825.926 | 3936.1378 | 4046.3497 | 4156.5616 | 4266.7734 | 4376.9853 | 4487.1971 | 4597.409 | 4707.6209 | 4817.8327 | 4928.0446 | 5038.2564 | 5148.4683 | 5258.6802 | 5368.892 | 5479.1039 | 5589.3157 | 5699.5276
2.2 | Gross actual savings, [USD] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3 | Net standard savings, [USD] | -22770 | 890.6218 | 670.1981 | 780.41 | 890.6218 | 1000.8337 | 1111.0456 | 1221.2574 | 1331.4693 | 1441.6811 | 1551.893 | 1662.1049 | 1772.3167 | 1882.5286 | 1992.7404 | 2102.9523 | 2213.1642 | 2323.376 | 2433.5879 | 2543.7997 | 2654.0116
2.4 | Net actual savings, [USD] | -22770 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516 | -3045.516
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | -22770 | 3784.7479 | 3435.3866 | 3401.2343 | 3364.6271 | 3325.8045 | 3284.991 | 3242.3971 | 3198.2203 | 3152.6452 | 3105.8448 | 3057.9807 | 3009.2041 | 2959.6559 | 2909.4676 | 2858.7617 | 2807.6523 | 2756.2455 | 2704.6397 | 2652.9264 | 2601.19
3.2 | Actualized actual net savings, [USD] | -22770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3 | Standardized NPV¹, [USD] | 2023: -2545.9337
3.4 | Actual NPV², [USD] | 2023: -64159.5563
3.5 | Accumulated net discounted standardized savings, [USD] | -22770 | -18985.2521 | -15549.8655 | -12148.6312 | -8784.0041 | -5458.1996 | -2173.2086 | 1069.1885 | 4267.4088 | 7420.0539 | 10525.8987 | 13583.8795 | 16593.0836 | 19552.7394 | 22462.207 | 25320.9687 | 28128.621 | 30884.8665 | 33589.5063 | 36242.4326 | 38843.6226
3.6 | Accumulated net discounted actual savings, [USD] | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770 | -22770
3.7 | Discounted payback period based on standardized conditions [years] | 2023: 7.6702
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: 2.945%
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: #NUM!
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | Installation of LED lighting and replacing of distribution system
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: 30000
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | 2138.9402 | 2019.1596 | 2079.0499 | 2138.9402 | 2198.8305 | 2258.7209 | 2318.6112 | 2378.5015 | 2438.3918 | 2498.2822 | 2558.1725 | 2618.0628 | 2677.9532 | 2737.8435 | 2797.7338 | 2857.6241 | 2917.5145 | 2977.4048 | 3037.2951 | 3097.1854
2.2 | Gross actual savings, [USD] | 0 | 1608.5349 | 1518.457 | 1563.4959 | 1608.5349 | 1653.5739 | 1698.6129 | 1743.6518 | 1788.6908 | 1833.7298 | 1878.7688 | 1923.8077 | 1968.8467 | 2013.8857 | 2058.9247 | 2103.9637 | 2149.0026 | 2194.0416 | 2239.0806 | 2284.1196 | 2329.1585
2.3 | Net standard savings, [USD] | -30000 | -906.5758 | -1026.3564 | -966.4661 | -906.5758 | -846.6855 | -786.7951 | -726.9048 | -667.0145 | -607.1242 | -547.2338 | -487.3435 | -427.4532 | -367.5628 | -307.6725 | -247.7822 | -187.8919 | -128.0015 | -68.1112 | -8.2209 | 51.6694
2.4 | Net actual savings, [USD] | -30000 | -1436.9811 | -1527.059 | -1482.0201 | -1436.9811 | -1391.9421 | -1346.9031 | -1301.8642 | -1256.8252 | -1211.7862 | -1166.7472 | -1121.7083 | -1076.6693 | -1031.6303 | -986.5913 | -941.5523 | -896.5134 | -851.4744 | -806.4354 | -761.3964 | -716.3575
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | -30000 | 2056.6733 | 1866.8265 | 1848.2678 | 1828.3751 | 1807.2784 | 1785.0999 | 1761.9539 | 1737.9478 | 1713.1818 | 1687.7499 | 1661.7401 | 1635.2343 | 1608.3093 | 1581.0364 | 1553.4823 | 1525.7089 | 1497.7739 | 1469.7307 | 1441.6291 | 1413.515
3.2 | Actualized actual net savings, [USD] | -30000 | 1546.6682 | 1403.8988 | 1389.9422 | 1374.9824 | 1359.1172 | 1342.4384 | 1325.0321 | 1306.9789 | 1288.3542 | 1269.2289 | 1249.6688 | 1229.7359 | 1209.4876 | 1188.9777 | 1168.2563 | 1147.3701 | 1126.3623 | 1105.2731 | 1084.14 | 1062.9976
3.3 | Standardized NPV¹, [USD] | 2023: -37908.042
3.4 | Actual NPV², [USD] | 2023: -46210.6457
3.5 | Accumulated net discounted standardized savings, [USD] | -30000 | -27943.3267 | -26076.5002 | -24228.2324 | -22399.8573 | -20592.5789 | -18807.479 | -17045.5251 | -15307.5773 | -13594.3955 | -11906.6456 | -10244.9055 | -8609.6712 | -7001.3619 | -5420.3256 | -3866.8433 | -2341.1344 | -843.3605 | 626.3702 | 2067.9993 | 3481.5143
3.6 | Accumulated net discounted actual savings, [USD] | -30000 | -28453.3318 | -27049.433 | -25659.4908 | -24284.5084 | -22925.3912 | -21582.9528 | -20257.9207 | -18950.9419 | -17662.5876 | -16393.3588 | -15143.6899 | -13913.9541 | -12704.4665 | -11515.4888 | -10347.2325 | -9199.8624 | -8073.5001 | -6968.227 | -5884.0869 | -4821.0894
3.7 | Discounted payback period based on standardized conditions [years] | 2023: 18.5738
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: #NUM!
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: #NUM!
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | Replacement of inneficient electrical equipment
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: 4170
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | 544.6387 | 514.1389 | 529.3888 | 544.6387 | 559.8886 | 575.1384 | 590.3883 | 605.6382 | 620.8881 | 636.138 | 651.3879 | 666.6377 | 681.8876 | 697.1375 | 712.3874 | 727.6373 | 742.8871 | 758.137 | 773.3869 | 788.6368
2.2 | Gross actual savings, [USD] | 0 | 233.2752 | 220.2118 | 226.7435 | 233.2752 | 239.8069 | 246.3386 | 252.8703 | 259.402 | 265.9337 | 272.4654 | 278.9972 | 285.5289 | 292.0606 | 298.5923 | 305.124 | 311.6557 | 318.1874 | 324.7191 | 331.2508 | 337.7825
2.3 | Net standard savings, [USD] | -4170 | -2500.8773 | -2531.3771 | -2516.1272 | -2500.8773 | -2485.6274 | -2470.3776 | -2455.1277 | -2439.8778 | -2424.6279 | -2409.378 | -2394.1281 | -2378.8783 | -2363.6284 | -2348.3785 | -2333.1286 | -2317.8787 | -2302.6289 | -2287.379 | -2272.1291 | -2256.8792
2.4 | Net actual savings, [USD] | -4170 | -2812.2408 | -2825.3042 | -2818.7725 | -2812.2408 | -2805.7091 | -2799.1774 | -2792.6457 | -2786.114 | -2779.5823 | -2773.0506 | -2766.5188 | -2759.9871 | -2753.4554 | -2746.9237 | -2740.392 | -2733.8603 | -2727.3286 | -2720.7969 | -2714.2652 | -2707.7335
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | -4170 | 523.691 | 475.3503 | 470.6247 | 465.5594 | 460.1876 | 454.5403 | 448.6466 | 442.5339 | 436.2277 | 429.752 | 423.1291 | 416.38 | 409.524 | 402.5795 | 395.5634 | 388.4915 | 381.3784 | 374.2378 | 367.0822 | 359.9235
3.2 | Actualized actual net savings, [USD] | -4170 | 224.3031 | 203.5982 | 201.5742 | 199.4046 | 197.1038 | 194.685 | 192.1607 | 189.5425 | 186.8415 | 184.0679 | 181.2312 | 178.3405 | 175.404 | 172.4296 | 169.4245 | 166.3955 | 163.3489 | 160.2905 | 157.2257 | 154.1595
3.3 | Standardized NPV¹, [USD] | 2023: -37034.1533
3.4 | Actual NPV², [USD] | 2023: -41908.0249
3.5 | Accumulated net discounted standardized savings, [USD] | -4170 | -3646.309 | -3170.9587 | -2700.3339 | -2234.7745 | -1774.5869 | -1320.0467 | -871.4001 | -428.8662 | 7.3615 | 437.1136 | 860.2427 | 1276.6227 | 1686.1467 | 2088.7262 | 2484.2896 | 2872.7811 | 3254.1595 | 3628.3973 | 3995.4795 | 4355.4031
3.6 | Accumulated net discounted actual savings, [USD] | -4170 | -3945.6969 | -3742.0987 | -3540.5246 | -3341.1199 | -3144.0161 | -2949.3311 | -2757.1705 | -2567.6279 | -2380.7864 | -2196.7185 | -2015.4873 | -1837.1468 | -1661.7428 | -1489.3132 | -1319.8887 | -1153.4932 | -990.1443 | -829.8538 | -672.6281 | -518.4686
3.7 | Discounted payback period based on standardized conditions [years] | 2023: 9.9831
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: #NUM!
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: #NUM!
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | #REF!
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: #REF!
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2.2 | Gross actual savings, [USD] | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2.3 | Net standard savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2.4 | Net actual savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.2 | Actualized actual net savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.3 | Standardized NPV¹, [USD] | 2023: #REF!
3.4 | Actual NPV², [USD] | 2023: #REF!
3.5 | Accumulated net discounted standardized savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.6 | Accumulated net discounted actual savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.7 | Discounted payback period based on standardized conditions [years] | 2023: #N/A
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: #VALUE!
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: #VALUE!
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | Installation of PV system
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: 7268
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | 1427.8245 | 1347.8663 | 1387.8454 | 1427.8245 | 1467.8036 | 1507.7827 | 1547.7618 | 1587.7409 | 1627.72 | 1667.699 | 1707.6781 | 1747.6572 | 1787.6363 | 1827.6154 | 1867.5945 | 1907.5736 | 1947.5526 | 1987.5317 | 2027.5108 | 2067.4899
2.2 | Gross actual savings, [USD] | 0 | 1427.8245 | 1347.8663 | 1387.8454 | 1427.8245 | 1467.8036 | 1507.7827 | 1547.7618 | 1587.7409 | 1627.72 | 1667.699 | 1707.6781 | 1747.6572 | 1787.6363 | 1827.6154 | 1867.5945 | 1907.5736 | 1947.5526 | 1987.5317 | 2027.5108 | 2067.4899
2.3 | Net standard savings, [USD] | -7268 | -1617.6915 | -1697.6497 | -1657.6706 | -1617.6915 | -1577.7124 | -1537.7333 | -1497.7542 | -1457.7751 | -1417.796 | -1377.817 | -1337.8379 | -1297.8588 | -1257.8797 | -1217.9006 | -1177.9215 | -1137.9424 | -1097.9634 | -1057.9843 | -1018.0052 | -978.0261
2.4 | Net actual savings, [USD] | -7268 | -1617.6915 | -1697.6497 | -1657.6706 | -1617.6915 | -1577.7124 | -1537.7333 | -1497.7542 | -1457.7751 | -1417.796 | -1377.817 | -1337.8379 | -1297.8588 | -1257.8797 | -1217.9006 | -1177.9215 | -1137.9424 | -1097.9634 | -1057.9843 | -1018.0052 | -978.0261
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | -7268 | 1372.9082 | 1246.1782 | 1233.7895 | 1220.5104 | 1206.4276 | 1191.6226 | 1176.1717 | 1160.1467 | 1143.6144 | 1126.6377 | 1109.2751 | 1091.5815 | 1073.608 | 1055.4023 | 1037.0089 | 1018.4691 | 999.8214 | 981.1016 | 962.3426 | 943.5754
3.2 | Actualized actual net savings, [USD] | -7268 | 1372.9082 | 1246.1782 | 1233.7895 | 1220.5104 | 1206.4276 | 1191.6226 | 1176.1717 | 1160.1467 | 1143.6144 | 1126.6377 | 1109.2751 | 1091.5815 | 1073.608 | 1055.4023 | 1037.0089 | 1018.4691 | 999.8214 | 981.1016 | 962.3426 | 943.5754
3.3 | Standardized NPV¹, [USD] | 2023: -26307.3632
3.4 | Actual NPV², [USD] | 2023: -26307.3632
3.5 | Accumulated net discounted standardized savings, [USD] | -7268 | -5895.0918 | -4648.9136 | -3415.1241 | -2194.6137 | -988.1861 | 203.4364 | 1379.6082 | 2539.7549 | 3683.3693 | 4810.007 | 5919.2822 | 7010.8637 | 8084.4718 | 9139.8741 | 10176.883 | 11195.3521 | 12195.1736 | 13176.2751 | 14138.6178 | 15082.1932
3.6 | Accumulated net discounted actual savings, [USD] | -7268 | -5895.0918 | -4648.9136 | -3415.1241 | -2194.6137 | -988.1861 | 203.4364 | 1379.6082 | 2539.7549 | 3683.3693 | 4810.007 | 5919.2822 | 7010.8637 | 8084.4718 | 9139.8741 | 10176.883 | 11195.3521 | 12195.1736 | 13176.2751 | 14138.6178 | 15082.1932
3.7 | Discounted payback period based on standardized conditions [years] | 2023: 6.8293
3.8 | Discounted actual payback period [years] | 2023: 6.8293
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: #NUM!
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: #NUM!
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | Installation of solar DHW system
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: 4000
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | 725.2645 | 684.6497 | 704.9571 | 725.2645 | 745.5719 | 765.8793 | 786.1867 | 806.4941 | 826.8015 | 847.1089 | 867.4163 | 887.7237 | 908.0311 | 928.3385 | 948.6459 | 968.9533 | 989.2607 | 1009.5681 | 1029.8755 | 1050.183
2.2 | Gross actual savings, [USD] | 0 | 173.5082 | 163.7918 | 168.65 | 173.5082 | 178.3665 | 183.2247 | 188.0829 | 192.9412 | 197.7994 | 202.6576 | 207.5159 | 212.3741 | 217.2323 | 222.0906 | 226.9488 | 231.807 | 236.6652 | 241.5235 | 246.3817 | 251.2399
2.3 | Net standard savings, [USD] | -4000 | -2320.2515 | -2360.8663 | -2340.5589 | -2320.2515 | -2299.9441 | -2279.6367 | -2259.3293 | -2239.0219 | -2218.7145 | -2198.4071 | -2178.0997 | -2157.7923 | -2137.4849 | -2117.1775 | -2096.8701 | -2076.5627 | -2056.2553 | -2035.9479 | -2015.6405 | -1995.333
2.4 | Net actual savings, [USD] | -4000 | -2872.0078 | -2881.7242 | -2876.866 | -2872.0078 | -2867.1495 | -2862.2913 | -2857.4331 | -2852.5748 | -2847.7166 | -2842.8584 | -2838.0001 | -2833.1419 | -2828.2837 | -2823.4254 | -2818.5672 | -2813.709 | -2808.8508 | -2803.9925 | -2799.1343 | -2794.2761
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | -4000 | 697.3697 | 632.9971 | 626.7043 | 619.9591 | 612.8057 | 605.2855 | 597.4373 | 589.2973 | 580.8998 | 572.2764 | 563.4571 | 554.4696 | 545.34 | 536.0924 | 526.7494 | 517.3321 | 507.86 | 498.3512 | 488.8226 | 479.2898
3.2 | Actualized actual net savings, [USD] | -4000 | 166.8349 | 151.4347 | 149.9292 | 148.3156 | 146.6042 | 144.8051 | 142.9276 | 140.9802 | 138.9712 | 136.9082 | 134.7983 | 132.6482 | 130.4641 | 128.2518 | 126.0166 | 123.7637 | 121.4976 | 119.2228 | 116.9432 | 114.6626
3.3 | Standardized NPV¹, [USD] | 2023: -34036.7599
3.4 | Actual NPV², [USD] | 2023: -42673.5763
3.5 | Accumulated net discounted standardized savings, [USD] | -4000 | -3302.6303 | -2669.6332 | -2042.929 | -1422.9698 | -810.1641 | -204.8786 | 392.5587 | 981.856 | 1562.7558 | 2135.0322 | 2698.4893 | 3252.9589 | 3798.2989 | 4334.3912 | 4861.1406 | 5378.4727 | 5886.3327 | 6384.684 | 6873.5066 | 7352.7964
3.6 | Accumulated net discounted actual savings, [USD] | -4000 | -3833.1651 | -3681.7304 | -3531.8012 | -3383.4856 | -3236.8814 | -3092.0762 | -2949.1486 | -2808.1684 | -2669.1972 | -2532.2889 | -2397.4906 | -2264.8424 | -2134.3783 | -2006.1265 | -1880.1099 | -1756.3462 | -1634.8486 | -1515.6258 | -1398.6826 | -1284.02
3.7 | Discounted payback period based on standardized conditions [years] | 2023: 7.3429
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: #NUM!
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: #NUM!
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | #REF!
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: #REF!
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2.2 | Gross actual savings, [USD] | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2.3 | Net standard savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2.4 | Net actual savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.2 | Actualized actual net savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.3 | Standardized NPV¹, [USD] | 2023: #REF!
3.4 | Actual NPV², [USD] | 2023: #REF!
3.5 | Accumulated net discounted standardized savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.6 | Accumulated net discounted actual savings, [USD] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3.7 | Discounted payback period based on standardized conditions [years] | 2023: #N/A
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: #VALUE!
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: #VALUE!
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | Implementation of EMS system
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: 0
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | 143.6373 | 135.5936 | 139.6154 | 143.6373 | 147.6591 | 151.6809 | 155.7028 | 159.7246 | 163.7465 | 167.7683 | 171.7902 | 175.812 | 179.8338 | 183.8557 | 187.8775 | 191.8994 | 195.9212 | 199.9431 | 203.9649 | 207.9868
2.2 | Gross actual savings, [USD] | 0 | 143.6373 | 135.5936 | 139.6154 | 143.6373 | 147.6591 | 151.6809 | 155.7028 | 159.7246 | 163.7465 | 167.7683 | 171.7902 | 175.812 | 179.8338 | 183.8557 | 187.8775 | 191.8994 | 195.9212 | 199.9431 | 203.9649 | 207.9868
2.3 | Net standard savings, [USD] | 0 | -2901.8787 | -2909.9224 | -2905.9006 | -2901.8787 | -2897.8569 | -2893.8351 | -2889.8132 | -2885.7914 | -2881.7695 | -2877.7477 | -2873.7258 | -2869.704 | -2865.6822 | -2861.6603 | -2857.6385 | -2853.6166 | -2849.5948 | -2845.5729 | -2841.5511 | -2837.5292
2.4 | Net actual savings, [USD] | 0 | -2901.8787 | -2909.9224 | -2905.9006 | -2901.8787 | -2897.8569 | -2893.8351 | -2889.8132 | -2885.7914 | -2881.7695 | -2877.7477 | -2873.7258 | -2869.704 | -2865.6822 | -2861.6603 | -2857.6385 | -2853.6166 | -2849.5948 | -2845.5729 | -2841.5511 | -2837.5292
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | 0 | 138.1127 | 125.3639 | 124.1176 | 122.7817 | 121.365 | 119.8757 | 118.3213 | 116.7092 | 115.0461 | 113.3383 | 111.5916 | 109.8117 | 108.0035 | 106.1721 | 104.3217 | 102.4566 | 100.5807 | 98.6975 | 96.8104 | 94.9224
3.2 | Actualized actual net savings, [USD] | 0 | 138.1127 | 125.3639 | 124.1176 | 122.7817 | 121.365 | 119.8757 | 118.3213 | 116.7092 | 115.0461 | 113.3383 | 111.5916 | 109.8117 | 108.0035 | 106.1721 | 104.3217 | 102.4566 | 100.5807 | 98.6975 | 96.8104 | 94.9224
3.3 | Standardized NPV¹, [USD] | 2023: -39141.1564
3.4 | Actual NPV², [USD] | 2023: -39141.1564
3.5 | Accumulated net discounted standardized savings, [USD] | 0 | 138.1127 | 263.4766 | 387.5942 | 510.376 | 631.741 | 751.6166 | 869.938 | 986.6472 | 1101.6933 | 1215.0315 | 1326.6232 | 1436.4348 | 1544.4384 | 1650.6105 | 1754.9322 | 1857.3888 | 1957.9695 | 2056.6671 | 2153.4775 | 2248.3999
3.6 | Accumulated net discounted actual savings, [USD] | 0 | 138.1127 | 263.4766 | 387.5942 | 510.376 | 631.741 | 751.6166 | 869.938 | 986.6472 | 1101.6933 | 1215.0315 | 1326.6232 | 1436.4348 | 1544.4384 | 1650.6105 | 1754.9322 | 1857.3888 | 1957.9695 | 2056.6671 | 2153.4775 | 2248.3999
3.7 | Discounted payback period based on standardized conditions [years] | 2023: #N/A
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: #NUM!
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: #NUM!
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | Upon implementation of all the measures
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: 225458.75
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | 15021.3605 | 14180.1643 | 14600.7624 | 15021.3605 | 15441.9586 | 15862.5567 | 16283.1548 | 16703.7528 | 17124.3509 | 17544.949 | 17965.5471 | 18386.1452 | 18806.7433 | 19227.3414 | 19647.9395 | 20068.5376 | 20489.1357 | 20909.7338 | 21330.3319 | 21750.93
2.2 | Gross actual savings, [USD] | 0 | 4386.2576 | 4140.6272 | 4263.4424 | 4386.2576 | 4509.0728 | 4631.8881 | 4754.7033 | 4877.5185 | 5000.3337 | 5123.1489 | 5245.9641 | 5368.7793 | 5491.5945 | 5614.4098 | 5737.225 | 5860.0402 | 5982.8554 | 6105.6706 | 6228.4858 | 6351.301
2.3 | Net standard savings, [USD] | -225458.75 | 11975.8445 | 11134.6483 | 11555.2464 | 11975.8445 | 12396.4426 | 12817.0407 | 13237.6388 | 13658.2368 | 14078.8349 | 14499.433 | 14920.0311 | 15340.6292 | 15761.2273 | 16181.8254 | 16602.4235 | 17023.0216 | 17443.6197 | 17864.2178 | 18284.8159 | 18705.414
2.4 | Net actual savings, [USD] | -225458.75 | 1340.7416 | 1095.1112 | 1217.9264 | 1340.7416 | 1463.5568 | 1586.3721 | 1709.1873 | 1832.0025 | 1954.8177 | 2077.6329 | 2200.4481 | 2323.2633 | 2446.0785 | 2568.8938 | 2691.709 | 2814.5242 | 2937.3394 | 3060.1546 | 3182.9698 | 3305.785
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | -225458.75 | 14443.6158 | 13110.359 | 12980.0246 | 12840.3219 | 12692.1643 | 12536.4089 | 12373.8594 | 12205.2686 | 12031.3418 | 11852.7389 | 11670.0768 | 11483.9321 | 11294.8427 | 11103.3106 | 10909.8034 | 10714.7563 | 10518.5741 | 10321.6326 | 10124.2804 | 9926.8405
3.2 | Actualized actual net savings, [USD] | -225458.75 | 4217.5554 | 3828.2426 | 3790.1848 | 3749.3914 | 3706.1292 | 3660.6484 | 3613.1837 | 3563.955 | 3513.1681 | 3461.0158 | 3407.6783 | 3353.3237 | 3298.1094 | 3242.1817 | 3185.6774 | 3128.7234 | 3071.4379 | 3013.9307 | 2956.3036 | 2898.6509
3.3 | Standardized NPV¹, [USD] | 2023: -31714.1537
3.4 | Actual NPV², [USD] | 2023: -198188.8149
3.5 | Accumulated net discounted standardized savings, [USD] | -225458.75 | -211015.1342 | -197904.7752 | -184924.7506 | -172084.4287 | -159392.2644 | -146855.8554 | -134481.9961 | -122276.7275 | -110245.3857 | -98392.6467 | -86722.5699 | -75238.6379 | -63943.7952 | -52840.4846 | -41930.6813 | -31215.925 | -20697.3509 | -10375.7183 | -251.4378 | 9675.4027
3.6 | Accumulated net discounted actual savings, [USD] | -225458.75 | -221241.1946 | -217412.952 | -213622.7672 | -209873.3758 | -206167.2466 | -202506.5982 | -198893.4145 | -195329.4595 | -191816.2914 | -188355.2755 | -184947.5973 | -181594.2735 | -178296.1642 | -175053.9824 | -171868.3051 | -168739.5817 | -165668.1438 | -162654.2131 | -159697.9095 | -156799.2586
3.7 | Discounted payback period based on standardized conditions [years] | 2023: 20.0253
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: 2.488%
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: -11.2%
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Measure: | Total proposed for implementation
№ | Indicators | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
1 | Investments
1.1 | Estimated initial investment (I), [USD] | 2023: 164319.75
1.2 | Maintenance costs (CM), [USD] |  | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516 | 3045.516
2 | Economies
2.1 | Gross standard savings, [USD] | 0 | 11607.58 | 10957.5555 | 11282.5678 | 11607.58 | 11932.5922 | 12257.6045 | 12582.6167 | 12907.629 | 13232.6412 | 13557.6534 | 13882.6657 | 14207.6779 | 14532.6902 | 14857.7024 | 15182.7146 | 15507.7269 | 15832.7391 | 16157.7514 | 16482.7636 | 16807.7758
2.2 | Gross actual savings, [USD] | 0 | 3275.0453 | 3091.6427 | 3183.344 | 3275.0453 | 3366.7465 | 3458.4478 | 3550.1491 | 3641.8503 | 3733.5516 | 3825.2529 | 3916.9541 | 4008.6554 | 4100.3567 | 4192.0579 | 4283.7592 | 4375.4605 | 4467.1617 | 4558.863 | 4650.5643 | 4742.2655
2.3 | Net standard savings, [USD] | -164319.75 | 8562.064 | 7912.0395 | 8237.0518 | 8562.064 | 8887.0762 | 9212.0885 | 9537.1007 | 9862.113 | 10187.1252 | 10512.1374 | 10837.1497 | 11162.1619 | 11487.1742 | 11812.1864 | 12137.1986 | 12462.2109 | 12787.2231 | 13112.2354 | 13437.2476 | 13762.2598
2.4 | Net actual savings, [USD] | -164319.75 | 229.5293 | 46.1267 | 137.828 | 229.5293 | 321.2305 | 412.9318 | 504.6331 | 596.3343 | 688.0356 | 779.7369 | 871.4381 | 963.1394 | 1054.8407 | 1146.5419 | 1238.2432 | 1329.9445 | 1421.6457 | 1513.347 | 1605.0483 | 1696.7495
3 | Financial Indicators
3.1 | Actualized standardized net savings, [USD] | -164319.75 | 11161.1346 | 10130.876 | 10030.1617 | 9922.208 | 9807.721 | 9687.3629 | 9561.7546 | 9431.4781 | 9297.0782 | 9159.0649 | 9017.9149 | 8874.0737 | 8727.9571 | 8579.9529 | 8430.4225 | 8279.7022 | 8128.1047 | 7975.9204 | 7823.4189 | 7670.8495
3.2 | Actualized actual net savings, [USD] | -164319.75 | 3149.082 | 2858.3975 | 2829.9812 | 2799.5224 | 2767.2202 | 2733.2615 | 2697.8215 | 2661.0644 | 2623.1438 | 2584.2038 | 2544.3787 | 2503.7943 | 2462.568 | 2420.809 | 2378.6194 | 2336.0941 | 2293.3213 | 2250.383 | 2207.3551 | 2164.3081
3.3 | Standardized NPV¹, [USD] | 2023: -24012.1496
3.4 | Actual NPV², [USD] | 2023: -154443.977
3.5 | Accumulated net discounted standardized savings, [USD] | -164319.75 | -153158.6154 | -143027.7393 | -132997.5777 | -123075.3697 | -113267.6486 | -103580.2858 | -94018.5312 | -84587.0531 | -75289.975 | -66130.9101 | -57112.9952 | -48238.9215 | -39510.9643 | -30931.0114 | -22500.5889 | -14220.8868 | -6092.7821 | 1883.1384 | 9706.5572 | 17377.4067
3.6 | Accumulated net discounted actual savings, [USD] | -164319.75 | -161170.668 | -158312.2705 | -155482.2893 | -152682.7669 | -149915.5467 | -147182.2851 | -144484.4636 | -141823.3993 | -139200.2554 | -136616.0517 | -134071.673 | -131567.8786 | -129105.3107 | -126684.5017 | -124305.8823 | -121969.7881 | -119676.4668 | -117426.0838 | -115218.7287 | -113054.4207
3.7 | Discounted payback period based on standardized conditions [years] | 2023: 18.7639
3.8 | Discounted actual payback period [years] | 2023: #N/A
3.9 | Internal Rate of Return based on standardized conditions (IRR¹) | 2023: 2.435%
3.10 | Internal Rate of Return based on actual conditions (IRR²) | 2023: -13.8%
NOTES: 1. The calculation period of 20 years shall be adopted on the basis of the minimum service life (term of operation) of the technical systems included in the energy efficiency measure concerned, so that the calculation period is less than or equal to the service life of the technical systems. . 2. The annual discount rate of 4% has been adopted for the calculation, in accordance with international practices. 3. Maintenance costs are determined in% of the initial investment costs, in accordance with the provisions of the European standard SM SR EN 15459: 2011 “Energy performance of buildings. Procedure for economic evaluation of energy systems in buildings ”. Maintenance costs with a value of “0” mean that the technical systems (especially the elements of the building envelope) do not require substantial investments during the life period to maintain them in their initial functional state (their initial performance). 4. The annual rate of increase in prices for energy resources of 2.8% - for natural gas and 2% - for electricity has been adopted for the calculation, in accordance with Annex II to Delegated Regulation (EU) NO. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating the optimal levels of cost the minimum energy performance requirements of buildings and their elements ”and Chapter 9 at“ Guidelines no. 2012 / C115 / 01 on Delegated Regulation (EU) no. Commission Regulation (EC) No 244/2012 of 16 January 2012 supplementing Directive 2010/31 / EU of the European Parliament and of the Council on the energy performance of buildings by establishing a comparative methodological framework for calculating cost-optimal levels of requirements minimum energy performance of buildings and their elements ”, approved by the European Commission. 5. The savings are calculated based on the estimates regarding the reduction of energy consumption as a result of the implementation of the analyzed measure (package of measures) of energy efficiency.
Note on E6: Saidmurodjon Khamdamov: 4%-2%
Note on E8: Saidmurodjon Khamdamov: 2,8%-8% =$E8*(1.08+0.08*(F3-$F$3))
Note on E9: Saidmurodjon Khamdamov: 2,8%-8% =$E8*(1.08+0.08*(F3-$F$3))
Note on E13: Saidmurodjon Khamdamov: =E8/POWER(1+0.10,E$3-$D$3)
Note on E14: Saidmurodjon Khamdamov: 4%-10%
Note on D15: Saidmurodjon Khamdamov: =NPV(0.10,E13:X13)+D13
Note on D16: Saidmurodjon Khamdamov: 4%-10

## Measures_summary
Nr. | Description of the measure | Investment [USD] | Theoretical savings based on standardized conditions |  | Theoretical payback period |  | Actual savings based on standardized conditions |  | Actual payback period |  | Lifetime of the measure [years] | Net Present Value (NPV¹) | Internal Rate of Return (IRR¹) | CO2 emission reduction [tCO2 / y] | Proposed for implementation
|  |  | [kWh / y] | [USD] | Simple | Discounted | [kWh / y] | [USD] | Simple | Discounted
1 | Thermal insulation of walls | 76137.9 | 75263.8494 | 1647.2286 | 46.2218 | #N/A | 20391.5048 | 446.2895 | 170.602 | #N/A | 20 | -44223.418 | -3.196% | 14.9022 | Yes
2 | Replacement of windows and doors | 16623.75 | 12816.4551 | 280.5016 | 59.2644 | #N/A | -2202.8702 | -48.2121 | -344.8043 | #N/A | 20 | -53622.5251 | #NUM! | 2.5377 | Yes
3 | Thermal insulation of the roof | 15350.1 | 104445.3208 | 2285.8958 | 6.7151 | 8.8106 | 33965.2018 | 743.3642 | 20.6495 | #N/A | 20 | -20957.7998 | #NUM! | 20.6802 | Yes
4 | Mechanical ventilation with heat recovery | 20139 | 69138.1151 | 1274.8403 | 15.7973 | #N/A | -11834.1295 | -497.3225 | -40.4948 | #N/A | 20 | -41573.0747 | #NUM! | 13.6893 | No
5 | Heating system replacement | 18000 | 28166.4 | 616.4513 | 29.1994 | #N/A | 7098.5127 | 155.3584 | 115.8611 | #N/A | 20 | -49740.0471 | #NUM! | 5.5769 | Yes
6 | Replacement of gas boiler | 22770 | 179846.8612 | 3936.1378 | 5.7849 | 7.6702 |  |  |  |  | 20 | -2545.9337 | 2.945% | 35.6097 | Yes
7 | Installation of LED lighting and replacing of distribution system | 30000 | 23380.5611 | 2138.9402 | 14.0256 | 18.5738 | 17582.7488 | 1608.5349 | 18.6505 | #N/A | 20 | -37908.042 | #NUM! | 13.6776 | No
8 | Replacement of inneficient electrical equipment | 4170 | 5953.3958 | 544.6387 | 7.6565 | 9.9831 | 2549.9102 | 233.2752 | 17.8759 | #N/A | 20 | -37034.1533 | #NUM! | 3.4827 | Yes
9 | Installation of PV system | 7268 | 15607.42 | 1427.8245 | 5.0903 | 6.8293 | 15607.42 | 1427.8245 | 5.0903 | 6.8293 | 20 | -26307.3632 | #NUM! | 9.1303 | Yes
10 | Installation of solar DHW system | 4000 | 7927.8 | 725.2645 | 5.5152 | 7.3429 | 7927.8 | 173.5082 | 23.0537 | #N/A | 20 | -34036.7599 | #NUM! | 1.5697 | Yes
11 | Implementation of EMS system | 0 | 4970.9699 | 143.6373 | 0 | #N/A | 4970.9699 | 143.6373 | 0 | #N/A | 20 | -39141.1564 | #NUM! | 1.178 | Yes
Protective measures, other investments
1 | Elektr kabellarini va tarqatish shkaflarini almashtirish | 4000 | [12 empty] | No
2 | Ichki devorlarni gipslash va bo‘yash (fasad ichki qismi) | 5000 | [12 empty] | No
3 | Eski isitish quvurlarini (podvalda) demontaj qilish | 2000 | [12 empty] | No
4 | 0 | 0 | [12 empty] | Yes
5 | 0 | 0 | [12 empty] | Yes
6 | 0 | 0 | [12 empty] | Yes
7 | 0 | 0 | [12 empty] | Yes
8 | 0 | 0 | [12 empty] | Yes
9 | 0 | 0 | [12 empty] | Yes
10 | 0 | 0 | [12 empty] | Yes
11 | 0 | 0 | [12 empty] | Yes
12 | 0 | 0 | [12 empty] | Yes
13 | 0 | 0 | [12 empty] | Yes
Total |  | 225458.75 | 527517.1484 | 15021.3605 | 14.2769 | 20.0253 | 96057.0685 | 4386.2576 | 51.4012 | #N/A | #REF! | -31714.1537 | 2.488% | 122.0345
Total proposed for implementation |  | 164319.75 | 434998.4722 | 11607.58 | 14.1562 | 18.7639 | 90308.4491 | 3275.0453 | 50.1733 | #N/A |  | -24012.1496 | 2.435% | 94.6675
|  | Local heating | Electricity | District heating (Markaziy issiqlik) | Coal (Ko‘mir) | [6 empty] | USD | UZS
| Emission factor to CO2 (kgCO2/kWh) | 0.198 | 0.585 | 0,050 | 0.38 | [6 empty] | 1 | 12024
| Factor to primary | 1.36 | 2.789 | 1.36 | 1
| Energy cost [USD/kWh] | 0.021886 | 0.091484 | 0.050058 | 0.015602
|  | UZS with VAT | USD with VAT | Source
| Issiqlik energiyasi (1 Gkal) | 700000 | 58.2169 | https://lex.uz/uz/docs/-8195731 |  |  |  | Decision nr. 748 of 28.09.2022 (in place since 01.10.2022)
| Elektr energiyasi (kWh) | 1100 | 0.091484 | https://het.uz/oz/pages/calculator |  |  |  | Decision nr. 910 of 08.12.2022
| Tabiiy gaz (m3) | 2500 | 0.20792 | https://hududgaz.uz/page;jsessionid=B21BB394CB88E48358C217C8CEA6FF50?0&m=323
| Ko'mir (tonna) | 1200000 | 99.8004